## Commercial
Comparison of Commercial Building Performance Characteristics Between
2015, 2018 and 2021 International Energy Conservation Code |  |  |  | Commercial | Commercial | Commercial
and ASHRAE/IESNA Standard 90.1-2016 and Standard 90.1 2016 |  |  |  | Provisions | Provisions | Provisions |  | ASHRAE/IESNA |  | ASHRAE/IESNA
For Climate Zone 5A |  |  |  | 2015 IECC | 2018 IECC | 2021 IECC |  | Standard 90.1-2016 |  | Standard 90.1-2019
Administration
|  | Purpose |  | Regulate design and construction of buildings for effective use and conservation of energy over useful life of each building | Regulate design and construction of buildings for effective use and conservation of energy over useful life of each building | Regulate design and construction of buildings for effective use and conservation of energy over useful life of each building |  | Minimum energy-efficient requirements for design, construction and a plan for operation and maintenance; and criteria for determining compliance with these requirements |  | Minimum energy-efficient requirements for design, construction and a plan for operation and maintenance; and utilization of on-site, renewable energy resources
|  | Scope |  | Applies to commercial buildings and buildings sites and associated systems and equipment | Applies to commercial buildings and buildings sites and associated systems and equipment | Applies to commercial buildings and buildings sites and associated systems and equipment |  | Applies to commercial buildings, portions of buildings, associated systems and equipment and identified equipment that are part of industrial or manufacturing processes |  | Applies to new commercial buildings, new portions of buildings and their systems, new systems and equipment in existing buildings and new equipment or building systems identified equipment that are part of industrial or manufacturing processes
Criteria for determining compliance with requirements
|  | Applicability |  | Chapter 4 applies to buildings & building sites | Chapter 4 applies to buildings & building sites | Chapter 4 applies to buildings & building sites |  | New buildings and additions to and alterations of existing buildings; replacement of portions of existing buildings |  | New buildings and additions to and alterations of existing buildings; replacement of portions of existing buildings
|  |  |  | Chapter 5 controls the alteration, repair, addition and changes of occupancy of existing buildings & structures | Chapter 5 controls the alteration, repair, addition and changes of occupancy of existing buildings & structures | Chapter 5 controls the alteration, repair, addition and changes of occupancy of existing buildings & structures
|  |  | Change in space conditioning | Full compliance for non-conditioned or low-energy space to conditioned space | Full compliance for non-conditioned or low-energy space to conditioned space | Full compliance for non-conditioned or low-energy space to conditioned space |  | Full compliance for unconditioned or semiheated space to conditioned space |  | Full compliance for unconditioned or semiheated space converted to conditioned space
|  |  | Change of occupancy | Change resulting in increased energy use must comply | Change resulting in increased energy use must comply | Change resulting in increased energy use must comply |  | Compliance defined in each section |  | Compliance defined in each section
|  |  |  | LPD must comply with change from one lighting area or space type to another area or space type | LPD must comply with change from one lighting area or space type to another area or space type | LPD must comply with change from one lighting area or space type to another area or space type
|  |  | Compliance | Chapter 4 | Chapter 4 | Chapter 4
|  |  |  | Commercial buildings comply with one of: | Commercial buildings comply with one of: | Commercial buildings comply with either IECC or ASHRAE/IESNA Standard 90.1-2019 |  | New buildings comply with all individual section requirements, or Energy Cost Budget Method or Appendix G with Performance Cost Index |  | New buildings comply with all individual section requirements, or Energy Cost Budget Method or Appendix G with Performance Cost Index
|  |  |  | 1) Standard 90.1-2013; or | 1) Standard 90.1-2016; or | IECC compliance shall be one of: |  | Additions comply with all individual sections or Energy Cost Budget Method or Appendix G |  | Additions comply with all individual sections or Energy Cost Budget Method or Appendix G
|  |  |  | 2) Sections C402, C403, C404 and C405 plus C406; or | 2) Sections C402, C403, C404, C405 and C408 plus C406; or | 1) Prescriptive compliance with envelope, mechanical, service water heating, electric power, lighting systems and additional efficiency requirements plus maintenance information and system commissioning. |  | Modeling will be required when addition to existing building cannot comply by itself. Trade offs will be allowed by modification(s) to existing components of existing building |  | Modeling will be required when addition to existing building cannot comply by itself. Trade offs will be allowed by modification(s) to existing components of existing building
|  |  |  | 3) Using Total Building Performance where proposed energy cost ≤85% of standard reference design building | 3) Using Total Building Performance where proposed energy cost ≤85% energy cost of standard reference design building | Dwelling units & sleeping units in R-2 buildings without systems serving multiple units may comply with Section R406
[6 empty] | 2)Total Building Performance option |  | Alterations of existing building comply with appropriate sections or Energy Cost Budget Method or Appendix G |  | Alterations of existing building comply with appropriate sections or Energy Cost Budget Method or Appendix G
[5 empty] | Chapter 5 | Chapter 5
[5 empty] | Controls the alteration, repair, addition and changes of occupancy of existing buildings & structures | Controls the alteration, repair, addition and changes of occupancy of existing buildings & structures
| Building Documentation and Closeout Submittal Requirements |  |  |  | Chapter 1 | Chapter 1 |  | Section 4.2.2 |  | Section 4.2.2
[5 empty] | Construction documents shall specify the documents be provided to owner ≤90 days of receipt of certificate of occupancy | Construction documents shall specify the documents be provided to owner ≤90 days of receipt of certificate of occupancy |  | Construction documents shall show all pertinent data and features to determine compliance and to indicate compliance with requirements |  | Construction documents shall show all pertinent data and features to determine compliance and to indicate compliance with requirements
Information on construction documents for building permit application
Identify verification & testing (V&T) providers
Review of construction documents by V&T providers
To verify relevant sensor locations, devices and control sequences are properly specified
To verify performance and testing criteria are included and
To verify equipment to be tested is accessible to testing and maintenance
Functional performance tests and verification processes and system performance are incorporated
Activities to be completed prior to issuance of building permit
Copy of commissioning plan submitted to owner and submitted to building official if requested
Commissioning provider designated by owner to manage commissioning activities and identified in construction documents
Commissioning provider's design review report submitted to owner
Construction phase commissioning requirements incorporated into construction documents
Activities prior to building occupancy
Verification and functional performance tests of specified systems completed
Verification and functional performance tests or preliminary commissioning report submitted to owner
Owner provides building official with one of:
Letter of transmittal acknowledging receipt and acceptance of all required verification documentation, FPT documentation and required preliminary commissioning report or
Copy of reports if requested by building official
Record documents
[5 empty] | Record of completed work | Record of completed work |  | IECC requirement in Section C103.6 and in each section of Standard 90.1 |  | IECC requirement in Section C103.6 and in each applicable section of Standard 90.1
[5 empty] | Updated mechanical, electrical & control drawings that indicate changes to | Updated mechanical, electrical & control drawings that indicate changes to
[5 empty] | Size, type and location of | Size, type and location of:
[5 empty] | Components | Components
[5 empty] | Equipment | Equipment
[5 empty] | Assemblies | Assemblies
|  |  | Compliance documentation |  | Energy code compliance documentation | Energy code compliance documentation |  | IECC requirement in Section C103.6 |  | IECC requirement in Section C103.6 and in each applicable section of Standard 90.1
[5 empty] | Supporting calculations | Supporting calculations
[5 empty] | Documentation includes | Documentation includes:
[5 empty] | Energy code edition used for each system | Energy code edition used for each system
[5 empty] | Each fenestration product installed | Each fenestration product installed
[5 empty] | Interior lighting power compliance path | Interior lighting power compliance path
[5 empty] | Envelope insulation compliance path | Envelope insulation compliance path
[5 empty] | System compliance calculations for: | System compliance calculations for:
[5 empty] | Envelope component performance alternative, | Envelope component performance alternative,
[5 empty] | Allowable fan horsepower, | Allowable fan horsepower,
[5 empty] | Interior lighting power requirement, | Interior lighting power requirement,
[5 empty] | Exterior lighting power requirement | Exterior lighting power requirement
|  |  | System operation control |  | Training for those responsible for maintaining and operating equipment | Training for those responsible for maintaining and operating equipment |  | IECC requirement in Section C103.6 |  | IECC requirement in Section C103.6 and in each applicable section of Standard 90.1
[5 empty] | Training to include: | Training to include:
[5 empty] | 1) Review of manuals and permanent certificate | 1) Review of manuals and permanent certificate
[5 empty] | 2) Hands-on demonstration of all: | 2) Hands-on demonstration of all:
[5 empty] | Normal maintenance procedures, | Normal maintenance procedures,
[5 empty] | Normal operating modes, | Normal operating modes,
[5 empty] | Emergency shutdown & startup procedures. | Emergency shutdown & startup procedures.
[5 empty] | 3) Training completion report | 3) Training completion report
Building Envelope |  |  |  | Climate Zone 5A | Climate Zone 5A | Climate Zone 5A |  | Climate Zone 5A |  | Climate Zone 5A
On construction documents
[5 empty] | Building thermal envelope depiction | Space conditioning categories indicated on floor plans |  | Space conditioning categories indicated on floor plans |  | Space conditioning categories indicated on floor plans
[5 empty] | Daylight zones | Daylight areas identified on floor plans |  | Daylight areas identified on floor plans |  | Daylight areas identified on floor plans
Roofs - Non Residential
Insulation entirely above deck
|  |  | Assembly maximum | U-0.032 | U-0.032 | U-0.032 |  | U-0.032 |  | U-0.032
|  |  | Insulation minimum R-Value | R-30 ci | R-30 ci | R-30 ci |  | R-30 ci |  | R-30 ci
Metal building
|  |  | Assembly maximum | U-0.035 | U-0.035 | U-0.035 |  | U-0.037 |  | U-0.037
|  |  | Insulation minimum R-Value | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS |  | R-19 + R-11 LS or |  | R-19 + R-11 LS or
[8 empty] | R-25 + R-8 LS |  | R-25 + R-8 LS
Attic and other
|  |  | Assembly maximum | U-0.027 | U-0.027 | U-0.021 |  | U-0.021 |  | U-0.021
|  |  | Insulation minimum R-Value | R-38 | R-38 | R-49 |  | R-49 |  | R-49
Roofs - Residential
Insulation entirely above deck
|  |  | Assembly maximum | U-0.032 | U-0.032 | U-0.032 |  | U-0.032 |  | U-0.032
|  |  | Insulation minimum R-Value | R-30 ci | R-30 ci | R-30 ci |  | R-30 ci |  | R-30 ci
Metal building
|  |  | Assembly maximum | U-0.035 | U-0.035 | U-0.035 |  | U-0.037 |  | U-0.037
|  |  | Insulation minimum R-Value | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS |  | R-19 + R-11 LS or |  | R-19 + R-11 LS or
[8 empty] | R-25 + R-8 LS |  | R-25 + R-8 LS
Attic and other
|  |  | Assembly maximum | U-0.021 | U-0.021 | U-0.021 |  | U-0.021 |  | U-0.021
|  |  | Insulation minimum R-Value | R-49 | R-49 | R-49 |  | R-49 |  | R-49
Roofs - Semiheated
Insulation entirely above deck
|  |  | Assembly maximum |  |  |  |  | U-0.063 |  | U-0.063
|  |  | Insulation minimum R-Value |  |  |  |  | R-15 ci |  | R-15 ci
Metal building
|  |  | Assembly maximum |  |  |  |  | U-0.082 |  | U-0.082
|  |  | Insulation minimum R-Value |  |  |  |  | R-19 |  | R-19
Attic and other
|  |  | Assembly Maximum |  |  |  |  | U-0.034 |  | U-0.034
|  |  | Insulation Minimum R-Value |  |  |  |  | R-30 |  | R-30
| Skylight Curbs |  | Insulation | R-5 | R-5 | R-5 |  | R-5 |  | R-5
Walls, Above Grade - Non Residential
Mass
|  |  | Assembly maximum | U-0.090 | U-0.090 | U-0.090 |  | U-0.090 |  | U-0.090
|  |  | Insulation minimum R-Value | R-11.4 ci | R-11.4 ci | R-11.4 ci |  | R-11.4 ci |  | R-11.4 ci
Metal building
|  |  | Assembly maximum | U-0.052 | U-0.052 | U-0.050 |  | U-0.050 |  | U-0.050
|  |  | Insulation minimum R-Value | R-13 + R-13 ci | R-13 + R-13 ci | R-13 + R-14 ci |  | R-0 + R-19 ci |  | R-0 + R-19 ci
Metal framed
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.055 |  | U-0.055 |  | U-0.055
|  |  | Insulation minimum R-Value | R-13 + R-7.5 ci | R-13 + R-7.5 ci | R-13 + R-10 ci |  | R-13 + R-10 ci |  | R-13 + R-10 ci
Wood framed and other
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.051 |  | U-0.051 |  | U-0.051
|  |  | Insulation minimum R-Value | R-13 + R-3.8 ci or | R-13 + R-3.8 ci or | R-13.0 + R-7.5 ci or |  | R-13.0 + R-7.5 ci or |  | R-13.0 + R-7.5 ci or
|  |  |  | R-20 | R-20 | R-20 + R-3.8 ci |  | R-19 + R-5 ci |  | R-19 + R-5 ci
Walls, Above Grade - Residential
Mass
|  |  | Assembly maximum | U-0.080 | U-0.080 | U-0.080 |  | U-0.080 |  | U-0.080
|  |  | Insulation minimum R-Value | R-13.3 ci | R-13.3 ci | R-13.3 ci |  | R-13.3 ci |  | R-13.3 ci
Metal building
|  |  | Assembly maximum | U-0.052 | U-0.052 | U-0.050 |  | U-0.050 |  | U-0.050
|  |  | Insulation minimum R-Value | R-13 + R-13 ci | R-13 + R-13 ci | R-13 + R-14 ci |  | R-0 + R-19 ci |  | R-0 + R-19 ci
Metal framed
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.055 |  | U-0.055 |  | U-0.055
|  |  | Insulation minimum R-Value | R-13 + R-7.5 ci | R-13 + R-7.5 ci | R-13 + R-10 ci |  | R-13 + R-10 ci |  | R-13 + R-10 ci
Wood framed and other
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.051 |  | U-0.051 |  | U-0.051
|  |  | Insulation minimum R-Value | R-13 + R-7.5 ci or | R-13 + R-7.5 ci or | R-13 + R-7.5 ci or |  | R-13 + R-7.5 ci or |  | R-13 + R-7.5 ci or
|  |  |  | R-20 + R-3.8 ci | R-20 + R-3.8 ci | R-20 + R-3.8 ci |  | R-19 + R-5 ci |  | R-19 + R-5 ci
Walls, Above Grade - Semiheated
Mass
|  |  | Assembly maximum |  |  |  |  | U-0.151 |  | U-0.151 (alternate available)
|  |  | Insulation minimum R-Value |  |  |  |  | R-5.7 ci |  | R-5.7 ci
Metal building
|  |  | Assembly maximum |  |  |  |  | U-0.094 |  | U-0.094
|  |  | Insulation minimum R-Value |  |  |  |  | R-0 + R-9.8 ci |  | R-0 + R-9.8 ci
Steel framed
|  |  | Assembly maximum |  |  |  |  | U-0.084 |  | U-0.084
|  |  | Insulation minimum R-Value |  |  |  |  | R-13 + R-3.8 ci |  | R-13 + R-3.8 ci
Wood framed and Other
|  |  | Assembly maximum |  |  |  |  | U-0.089 |  | U-0.089
|  |  | Insulation minimum R-Value |  |  |  |  | R-13 |  | R-13
Wall, Below Grade - Non Residential
Below grade wall
|  |  | Assembly maximum | C-0.119 | C-0.119 | C-0.119 |  | C-0.119 |  | C-0.119
|  |  | Insulation minimum R-Value | R-7.5 ci | R-7.5 ci | R-7.5 ci |  | R-7.5 ci |  | R-7.5 ci
Wall, Below Grade - Residential
Below grade wall
|  |  | Assembly maximum | C-0.119 | C-0.119 | C-0.092 |  | C-0.092 |  | C-0.092
|  |  | Insulation minimum R-Value | R-7.5 ci | R-7.5 ci | R-10 ci |  | R-10 ci |  | R-10 ci
Wall, Below Grade - Semiheated
Below grade wall
|  |  | Assembly maximum |  |  |  |  | C-1.140 |  | C-1.140
|  |  | Insulation minimum R-Value |  |  |  |  | NR |  | NR
Floors - Non Residential
Mass
|  |  | Assembly maximum | U-0.074 | U-0.074 | U-0.057 |  | U-0.057 |  | U-0.057
|  |  | Insulation minimum R-Value | R-10 ci | R-10 ci | R-14.6 ci |  | R-14.6 ci |  | R-14.6 ci
|  | Joist / framing | [5 empty] | Steel joists |  | Steel joists
|  |  | Assembly maximum | U-0.033 | U-0.033 | U-0.033 |  | U-0.038 |  | U-0.038
|  |  | Insulation minimum R-Value | R-30 | R-30 | R-30 |  | R-30 |  | R-30
Wood framed and other
|  |  | Assembly maximum |  |  |  |  | U-0.033 |  | U-0.033
|  |  | Insulation minimum R-Value |  |  |  |  | R-30 |  | R-30
Floors - Residential
Mass
|  |  | Assembly Maximum | U-0.064 | U-0.064 | U-0.051 |  | U-0.051 |  | U-0.051
|  |  | Insulation Minimum R-Value | R-12.5 ci | R-12.5 ci | R-16.7 ci |  | R-16.7 ci |  | R-16.7 ci
|  | Joists / framing | [5 empty] | Steel joists |  | Steel joists
|  |  | Assembly maximum | U-0.033 | U-0.033 | U-0.033 |  | U-0.038 |  | U-0.038
|  |  | Insulation minimum R-Value | R-30 | R-30 | R-30 |  | R-30 |  | R-30
Wood framed and other
|  |  | Assembly maximum |  |  |  |  | U-0.033 |  | U-0.033
|  |  | Insulation minimum R-Value |  |  |  |  | R-30 |  | R-30
Floors - Semiheated
Mass
|  |  | Assembly maximum |  |  |  |  | U-0.107 |  | U-0.107
|  |  | Insulation minimum R-Value |  |  |  |  | R-6.3 ci |  | R-6.3 ci
Steel joist
|  |  | Assembly maximum |  |  |  |  | U-0.052 |  | U-0.052
|  |  | Insulation minimum R-Value |  |  |  |  | R-19 |  | R-19
Wood framed and other
|  |  | Assembly maximum |  |  |  |  | U-0.051 |  | U-0.051
|  |  | Insulation minimum R-Value |  |  |  |  | R-19 |  | R-19
Slab-On-Grade Floors - Non Residential
Unheated
|  |  | Assembly maximum | F-0.54 | F-0.54 | F-0.520 |  | F-0.520 |  | F-0.520
|  |  | Insulation minimum R-Value | R-10 for 24" Below | R-10 for 24" Below | R-15 for 24" |  | R-15 for 24" |  | R-15 for 24"
Heated
|  |  | Assembly maximum | F-0.65 | F-0.79 | F-0.62 |  | F-0.688 |  | F-0.688
plus F-0.64 full slab
|  |  | Insulation minimum R-Value | R-15 for 36" Below | R-15 for 36" Below | R-15 for 36" Below plus R-5 full slab |  | R-20 for 48" |  | R-20 for 48"
plus R-5 full slab
Slab-On-Grade Floors - Residential
Unheated
|  |  | Assembly maximum | F-0.54 | F-0.54 | F-0.510 |  | F-0.510 |  | F-0.510
|  |  | Insulation minimum R-Value | R-10 for 24" Below | R-10 for 24" Below | R-20 for 24" Below |  | R-20 for 24" |  | R-20 for 24"
Heated
|  |  | Assembly maximum | F-0.65 | F-0.79 | F-0.62 |  | F-0.688 |  | F-0.688
plus F-0.64 full slab
|  |  | Insulation minimum R-Value | R-15 for 36" Below | R-15 for 36" Below | R-15 for 36" Below plus R-5 full slab |  | R-20 for 48" |  | R-20 for 48"
plus R-5 full slab
Slab-On-Grade Floors - Semiheated
Unheated
|  |  | Assembly maximum |  |  |  |  | F-0.730 |  | F-0.730
|  |  | Insulation minimum R-Value |  |  |  |  | NR |  | NR
Heated
|  |  | Assembly maximum |  |  |  |  | F-0.900 |  | F-0.900
|  |  | Insulation minimum R-Value |  |  |  |  | R-10 for 24" |  | R-10 for 24"
Opaque Doors - Non Residential
|  | Swinging | Assembly Maximum | U-0.37 | U-0.37 | U-0.370 |  | U-0.370 |  | U-0.370
|  | Garage door <14% glazing | Assembly Maximum |  | U-0.31 | U-0.310
|  | Non-swinging, horizontally hinged, sectional | Assembly maximum |  |  | U-0.440
|  | Non-swinging | Insulation minimum R-Value | R-4.75 | R-4.75 | U-0.310 |  | U-0.310 |  | U-0.310
Opaque Doors - Residential
|  | Swinging | Assembly maximum | U-0.37 | U-0.37 | U-0.370 |  | U-0.370 |  | U-0.370
|  | Garage door <14% glazing | Assembly maximum |  | U-0.31 | U-0.310
|  | Non-swinging | Insulation minimum R-Value | R-4.75 | R-4.75 | U-0.310 |  | U-0.310 |  | U-0.310
Opaque Doors - Semiheated
|  | Swinging | Assembly maximum |  |  |  |  | U-0.370 |  | U-0.370
|  | Non-swinging | Assembly maximum |  |  |  |  | U-0.360 |  | U-0.360
Fenestration - Non Residential
Vertical glazing, 0-40% of wall
|  |  | Nonmetal framing, all |  |  |  |  | U-0.31
|  |  | Fixed | [6 empty] | U-0.36
|  |  | Metal framing, fixed |  |  |  |  | U-0.38
|  |  | Operable | [6 empty] | U-0.45
|  |  | Metal framing, operable |  |  |  |  | U-0.46
|  |  | Entrance door | [6 empty] | U-0.63
|  |  | Metal framing, entrance door |  |  |  |  | U-0.68
|  |  | Solar Heat Gain Coefficient, all |  |  |  |  | SHGC-0.38
|  |  | Solar Heat Gain Coefficient, Fixed | [6 empty] | SHGC-0.38
|  |  | Solar Heat Gain Coefficient, Operable | [6 empty] | SHGC-0.33
|  |  | Solar Heat Gain Coefficient, Entrance door | [6 empty] | SHGC-0.33
|  |  | VT/SHGC, all |  |  |  |  | 1.1 |  | 1.1
Skylight, all types, 0-3% of roof
|  |  | Assembly maximum |  |  |  |  | U-0.50 |  | U-0.50
|  |  | Assembly maximum |  |  |  |  | SHGC-0.40 |  | SHGC-0.40
Fenestration - Residential
Vertical glazing, 0-40% of wall
|  |  | Nonmetal framing, all |  |  |  |  | U-0.31
|  |  | Fixed | [6 empty] | U-0.36
|  |  | Metal framing, fixed |  |  |  |  | U-0.38
|  |  | Operable | [6 empty] | U-0.45
|  |  | Metal framing, operable |  |  |  |  | U-0.46
|  |  | Entrance door | [6 empty] | U-0.63
|  |  | Metal framing, entrance door |  |  |  |  | U-0.68
|  |  | Sola Heat Gain Coefficient, all |  |  |  |  | SHGC-0.38
|  |  | Solar Heat Gain Coefficient, Fixed | [6 empty] | SHGC-0.38
|  |  | Solar Heat Gain Coefficient, Operable | [6 empty] | SHGC-0.33
|  |  | Solar Heat Gain Coefficient, Entrance door | [6 empty] | SHGC-0.33
|  |  | VT/SHGC, all |  |  |  |  | 1.1 |  | 1.1
Skylight, all types, 0-3% of roof
|  |  | Assembly maximum |  |  |  |  | U-0.50 |  | U-0.50
|  |  | Assembly maximum |  |  |  |  | SHGC-0.40 |  | SHGC-0.40
Fenestration - Semiheated
Vertical glazing, 0-40% of wall
|  |  | Nonmetal framing, all |  |  |  |  | U-0.45
|  |  | Fixed | [6 empty] | U-0.50
|  |  | Metal framing, fixed |  |  |  |  | U-0.62
|  |  | Operable | [6 empty] | U-0.65
|  |  | Metal framing, operable |  |  |  |  | U-0.70
|  |  | Entrance door | [6 empty] | U-0.77
|  |  | Metal framing, entrance door |  |  |  |  | U-0.77
|  |  | Sola Heat Gain Coefficient, all |  |  |  |  | NR |  | NR
|  |  | VT/SHGC, all |  |  |  |  | NR |  | NR
Skylight, all types, 0-3% of roof
|  |  | Assembly maximum |  |  |  |  | U-0.98 |  | U-0.75
|  |  | Assembly maximum |  |  |  |  | NR |  | NR
Fenestration
|  | Vertical | Fixed fenestration | U-0.38 | U-0.38 | U-0.36
|  |  | Operable fenestration | U-0.45 | U-0.45 | U-0.45
|  |  | Entrance doors | U-0.77 | U-0.77 | U-0.63
Solar Heat Gain Coefficient by orientation
|  |  | PF <0.2 | SHGC-0.40 (SEW) | SHGC-0.38 (SEW) | 0.38 | Fixed | Table for SHGC multipliers for permanent projections by orientation for 0.1 increments in PF |  | Table for SHGC multipliers for permanent projections by orientation for 0.1 increments in PF
|  |  |  | SHGC-0.53 (N) | SHGC-0.51 (N) | 0.33 | Operable
|  |  | 0.2 ≤ PF < 0.5 | SHGC-0.48 (SEW) | SHGC-0.46 (SEW) | 0.46 | Fixed
|  |  |  | SHGC-0.58 (N) | SHGC-0.56 (N) | 0.4 | Operable
|  |  | PF ≥ 0.5 | SHGC-0.64 (SEW) | SHGC-0.61 (SEW) | 0.61 | Fixed
|  |  |  | SHGC-0.64 (N) | SHGC-0.61 (N) | 0.53 | Operable
|  |  | Maximum area (percentage of gross above-grade wall area) | ≤30% | ≤30% | ≤30% |  | ≤40% |  | ≤40%
|  |  | Maximum Increased Fenestration Area: | ≤40% When | ≤40% When | ≤40% When |  | ≥40% When vertical fenestration on street side of street-level story only, provided: |  | ≥40% When vertical fenestration on street side of street-level story only, provided:
|  |  |  | 1) For buildings ≤2 stories; ≥50% net floor area in daylight zone | 1) For buildings ≤2 stories; ≥50% net floor area in daylight zone | 1) For buildings ≤2 stories; ≥50% net floor area in daylight zone |  | a) Street side of street-level story ≤20 ft in height |  | a) Street side of street-level story ≤20 ft in height
|  |  |  | 2) For buildings ≥3 stories; ≥25% net floor area in daylight zone | 2) For buildings ≥3 stories; ≥25% net floor area in daylight zone | 2) For buildings ≥3 stories; ≥25% net floor area in daylight zone |  | b) Fenestration has continuous overhang with weighted average PF >0.5 |  | b) Fenestration has continuous overhang with weighted average PF >0.5
|  |  |  | 3) Daylight responsive lighting controls installed in daylight zone | 3) Daylight responsive lighting controls installed in daylight zone | 3) Daylight responsive lighting controls installed in daylight zone |  | c) Fenestration area for street side of street-level story <75% gross wall area for street side of street-level story |  | c) Fenestration area for street side of street-level story <75% gross wall area for street side of street-level story
|  |  |  | 4) Visible Transmittance ≥1.1 times SHGC | 4) Visible Transmittance ≥1.1 times SHGC | 4) Visible Transmittance ≥1.1 times SHGC
|  | Skylights | U-factors | U-0.50 | U-0.50 | U-0.50 |  | U-0.50 |  | U-0.50
|  |  |  | U-0.75 | U-0.75 | U-0.75 |  | U-075 |  | U-075
|  |  |  | When daylight responsive controls installed in daylight zone | When daylight responsive controls installed in daylight zone | When daylight responsive controls installed in daylight zone |  | When haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols |  | When haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols
|  |  | Solar Heat Gain Coefficient | SHGC-0.40 | SHGC-0.40 | SHGC-0.40 |  | SHGC - 0.40 |  | SHGC - 0.40
|  |  |  | SHGC-0.60 | SHGC-0.60 | SHGC-0.60 |  | Except when |  | Except when
|  |  |  | When automated daylighting controls installed in daylight zone | When daylight responsive controls installed above daylight zones | When daylight responsive controls installed above daylight zones |  | Haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols |  | Haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols
|  |  | Maximum area (percentage of roof area) | ≤3% | ≤3% | ≤3% |  | ≤3% |  | ≤3%
|  |  | Maximum increased skylight area | ≤5% When | ≤6% When | ≤6% When |  | ≤6% When |  | ≤6% When
|  |  |  | Automatic daylighting controls installed in daylight zones under skylights | Daylight responsive controls installed in toplit zones | Daylight responsive controls installed in toplit zones |  | Total daylight area under skylights ≥50% floor area of space and haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols |  | Total daylight area under skylights ≥50% floor area of space and haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols
Insulation of Radiant Heating Systems
|  |  | Insulation on surfaces not facing the heated space |  |  |  |  | Radiant floor heating
|  |  | Insulation minimum R-value | R-3.5 | R-3.5 | R-3.5 |  | R-3.5 on bottom surface |  | R-3.5 on ineffective panel surface
[8 empty] | Adjacent envelope insulation counts toward requirement |  | R-3.5 on bottom surface of floors, adjacent envelope insulation counts toward requirement
Fenestration Orientation
|  |  | Comply with either |  |  |  |  | AW ≤ (AT)/4 and |  | AW ≤ (AT)/4 and
[8 empty] | AE ≤ (AT)/4 |  | AE ≤ (AT)/4
[8 empty] | AW x SHGCw ≤ (AT x SHGCc)/5 and |  | AW x SHGCw ≤ (AT x SHGCc)/5 and
[8 empty] | AE x SHGCE ≤ (AT x SHGCc)/5 |  | AE x SHGCE ≤ (AT x SHGCc)/5
Required Skylights
Required locations
|  |  | Enclosed space | >2,500 sq ft | >2,500 sq ft | ≥2,500 sq ft |  | ≥2,500 sq ft |  | ≥2,500 sq ft
|  |  |  | Under roof with ≥75% of ceiling area with ceiling height >15 ft | Under roof with ≥75% of ceiling area with ceiling height >15 ft | Directly under roof with ≥75% of ceiling area with ceiling height >15 ft |  | Under roof with ceiling heights >15 ft |  | Under roof with ceiling heights >15 ft
|  |  | Defined space type | Office, Lobby, Atrium, Concourse, Corridor, Storage space, Gymnasium/exercise center, Convention center, Automotive service area, Space where manufacturing occurs, Nonrefrigerated warehouse, Retail store, Distribution/sorting area, Transportation depot or Workshop | Office, Lobby, Atrium, Concourse, Corridor, Storage space, Gymnasium/exercise center, Convention center, Automotive service area, Space where manufacturing occurs, Nonrefrigerated warehouse, Retail store, Distribution/sorting area, Transportation depot or Workshop | Office, Lobby, Atrium, Concourse, Corridor, Storage space, Gymnasium/exercise center, Convention center, Automotive service area, Space where manufacturing occurs, Nonrefrigerated warehouse, Retail store, Distribution/sorting area, Transportation depot or Workshop |  | Office, Lobby, Atrium, Concourse, Corridor, Storage (including nonrefrigerated warehouse), Gymnasium, Fitness/exercise area, Playing area, Gymnasium seating area, Convention exhibit/event space, Courtroom, Automotive service, Fire station engine room, Manufacturing corridor/transition and bay areas, Retail, Library reading and stack areas, Distribution/sorting area, Transportation baggage and seating areas, or Workshop |  | Office, Lobby, Atrium, Concourse, Corridor, Storage (including nonrefrigerated warehouse), Gymnasium, Fitness/exercise area, Playing area, Gymnasium seating area, Convention exhibit/event space, Courtroom, Automotive service, Fire station engine room, Manufacturing corridor/transition and bay areas, Retail, Library reading and stack areas, Distribution/sorting area, Transportation baggage and seating areas, or Workshop
|  |  | Minimum skylight fenestration area | Total daylight zone under skylight ≥50% floor area | Total daylight zone under skylight ≥50% floor area | Total daylight zone under skylight ≥50% floor area |  | Total daylight zone under skylight ≥50% floor area |  | Total daylight zone under skylight ≥50% floor area
|  |  |  | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or |  | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or |  | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or
|  |  |  | Skylight effective aperture ≥1% | Skylight effective aperture ≥1% | Skylight effective aperture ≥1% or ≥0.66% for tubular skylight device |  | Skylight effective aperture ≥1% |  | Skylight effective aperture ≥1%
|  |  |  | Haze value >90% | Haze value >90% | Haze factor >90% |  | Haze value >90% |  | Haze value >90%
|  |  | Lighting controls | Daylight responsive control of all lighting in daylight zone | Daylight responsive control of all lighting in daylight zone | Daylight responsive control of all lighting in daylight zone |  | Daylight responsive control of all lighting in daylight zone |  | Daylight responsive control of all lighting in daylight zone
|  |  | Exceptions | Space LPD <0.5 w/sf | Space LPD <0.5 w/sf | Space LPD <0.5 w/sf
|  |  |  | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm |  | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm |  | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm
|  |  |  | Daylight area under roof monitors >50% enclosed space floor area | Daylight area under roof monitors >50% enclosed space floor area | Daylight area under roof monitors >50% enclosed space floor area |  | Daylight area under roof monitors >50% enclosed space floor area |  | Daylight area under roof monitors >50% enclosed space floor area
|  |  |  | Spaces where total area minus daylight zone adjacent to vertical fenestration <2,500 sf & when lighting is controlled | Spaces where total area minus daylight zone adjacent to vertical fenestration <2,500 sf & when lighting is controlled | Spaces where total area minus daylight zone adjacent to vertical fenestration <2,500 sf & when lighting is controlled |  | Enclosed spaces where total area minus primary & secondary sidelighted area(s) <2,500 sf and where lighting is controlled to sidelighting requirements |  | Enclosed spaces where total area minus primary & secondary sidelighted area(s) <2,500 sf and where lighting is controlled to sidelighting requirements
[6 empty] | Space designed as storm shelter |  | Enclosed space where 90% skylight area shaded on June 21 @ noon by permanent architectural features of building |  | Enclosed space where 90% skylight area shaded on June 21 @ noon by permanent architectural features of building
| Alternate Envelope Compliance Path |  |  | Component Performance Alternative | Component Performance Alternative | Component Performance Alternative |  | Building Envelope Performance Factor Trade-Off |  | Building Envelope Trade-Off Compliance Path
| Rigid Insulation |  |  | Joints To Be Staggered on Multiple Layers | Joints To Be Staggered on Multiple Layers | Joints To Be Staggered on Multiple Layers |  | Joints To Be Staggered on Multiple Layers |  | Joints To Be Staggered on Multiple Layers
Insulation Installation
|  |  | Eave Vent Baffles |  |  |  |  | Required with eave vents |  | Required with eave vents
|  |  | Substantial contact |  |  |  |  | In substantial contact with inside surface in accordance with manufacturers' recommendations for framing system used |  | In substantial contact with inside surface in accordance with manufacturers' recommendations for framing system used
|  |  | Recessed HVAC equipment in thermal envelope |  |  | Separated from exterior or unconditioned or exempt space ≥R-12 insulation |  | Not recessed in manner as to affect insulation thickness |  | Not recessed in manner as to affect insulation thickness
|  |  | Recessed lighting In thermal envelope |  |  |  |  | Not recessed in manner as to affect insulation thickness |  | Not recessed in manner as to affect insulation thickness
Comply with envelope air leakage requirements
|  |  | Extent of insulation |  |  |  |  | Over full component area
| Dynamic Glazing |  |  | Ratio of higher to lower labeled SHGC ≥2.4 & automatically controlled to modulate solar gain into space, Can not be used in averaging | Ratio of higher to lower labeled SHGC ≥2.4 & automatically controlled to modulate solar gain into space, Can not be used in averaging | Ratio of higher to lower labeled SHGC ≥2.4 & automatically controlled to modulate solar gain into space, Can not be used in averaging |  | Minimum SHGC used to demonstrate compliance, cannot be used in averaging |  | Light-to-solar-gain ratio (LSG) determined using maximum VT and maximum SHGC used to demonstrate compliance, cannot be used in averaging
Air Leakage
|  | Air barriers |  | Continuous throughout thermal envelope | Continuous throughout thermal envelope | Continuous throughout thermal envelope |  | Continuous throughout thermal envelope |  | Continuous throughout thermal envelope and over all surfaces
|  |  | Air barrier construction (design and installation) | Continuous for all assemblies | Continuous for all assemblies | Continuous for all assemblies |  | Continuous for all assemblies |  | Continuous for all assemblies including those used as ducts or plenums
|  |  |  | All joints and seams sealed including transitions in places and changes in materials | All joints and seams sealed including transitions in places and changes in materials | All joints and seams sealed including transitions in places and changes in materials |  | All joints and seams sealed including transitions in places and changes in materials |  | All joints and seams sealed including transitions in places and changes in materials
|  |  |  | All penetrations sealed | All penetrations sealed | All penetrations sealed |  | All penetrations sealed |  | All penetrations sealed
|  |  |  | Ability to resist positive and negative pressure | Ability to resist positive and negative pressure | Ability to resist positive and negative pressure |  | Ability to resist positive and negative pressure |  | Ability to resist positive and negative pressure
|  |  | Whole-Building Air Leakage / Building envelope performance verification and testing |  |  | Verification of continuous air barrier |  |  |  | Verification of continuous air barrier
[6 empty] | 1) Review construction documents 2) Inspect during construction while still accessible 3) Final commissioning report identifying deficiencies found during review of construction documents and inspections and details of corrective measures taken |  |  |  | 1) Review construction documents 2) Inspect during construction while still accessible 3) Final commissioning report identifying deficiencies found during review of construction documents and inspections and details of corrective measures taken
[6 empty] | Dwelling & sleeping units in buildings or portions of buildings, including Group R & I occupancies |  |  |  | Continuous air barrier design and installation verification by independent third party
Measured air leakage ≤0.30 cfm/sf of testing unit enclosure area @ 0.2" wg
[6 empty] | Where ≥8 dwelling units or sleeping units or other occupiable conditioned spaces (individual testing units) a weighted average of all test results is acceptable with rules. |  |  |  | Measured air leakage rate of completed building ≤0.40 cfm/sf under differential pressure of 0.3" water
[6 empty] | Buildings or portions of buildings other than Group R & I occupancies |  |  |  | Exceptions:
[6 empty] | Measured air leakage ≤0.40 cfm/sf of building thermal envelope area @ 0.3" wg |  |  |  | Less than whole building testing if building floor area ≥50,000 sf
[6 empty] | When measured leakage rate >0.40 but ≤ 0.60 cfm/sf, conduct diagnostic evaluation and seal any leaks without destruction of existing building components. Also visually inspect air barrier and seal leaks. Submit report of corrective actions to building official and building owner. |  |  |  | When measured leakage rate >0.40 but ≤ 0.60 cfm/sf, conduct diagnostic evaluation and seal any leaks without destruction of existing building components. Also visually inspect air barrier and seal leaks. Submit report of corrective actions to building official and building owner.
|  |  | Air barrier compliance options | Materials with air permeability ≤0.004 cfm/sf | Materials with air permeability ≤0.004 cfm/sf | Materials with air permeability ≤0.004 cfm/sf @ 0.3" wg |  | Materials with air permeability ≤0.004 cfm/sf |  | Materials with air permeability ≤0.004 cfm/sf
|  |  |  | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf @ 0.3" wg |  | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf |  | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf
|  |  |  | Tested air leakage rate of completed building ≤0.40 cfm/sf |  |  |  | Tested air leakage rate of completed building ≤0.40 cfm/sf under differential pressure of 0.3" water
Air leakage for fenestration
Maximum infiltration rate for fenestration assemblies
|  |  | Windows | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf |  | 0.20 cfm/sf |  | 0.20 cfm/sf
|  |  | Sliding doors | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf |  | 0.20 cfm/sf |  | 0.20 cfm/sf
|  |  | Swinging doors | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf |  | 0.20 cfm/sf |  | 0.20 cfm/sf
|  |  | Skylights - with condensation weepage openings | 0.30 cfm/sf | 0.30 cfm/sf | 0.30 cfm/sf |  | 0.30 cfm/sf |  | 0.30 cfm/sf
|  |  | Skylights - all other | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf |  | 0.50 cfm/sf |  | 0.50 cfm/sf
|  |  | Curtain wall | 0.06 cfm/sf | 0.06 cfm/sf | 0.06 cfm/sf |  | 0.06 cfm/sf |  | 0.06 cfm/sf
|  |  | Storefront glazing | 0.06 cfm/sf | 0.06 cfm/sf | 0.06 cfm/sf |  | 0.06 cfm/sf |  | 0.06 cfm/sf
|  |  | Commercial glazed swinging entrance doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf |  | 1.00 cfm/sf |  | 1.00 cfm/sf
|  |  | Power-operated sliding doors & power-operated folding doors |  | 1.00 cfm/sf | 1.00 cfm/sf |  | 1.00 cfm/sf |  | 1.00 cfm/sf
|  |  | Revolving doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf |  | 1.00 cfm/sf |  | 1.00 cfm/sf
|  |  | Garage doors | 0.40 cfm/sf | 0.40 cfm/sf | 0.40 cfm/sf |  | 0.40 cfm/sf |  | 0.40 cfm/sf
|  |  | Rolling doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf |  | 1.3 cfm/sf |  | 1.3 cfm/sf
|  |  | High-speed doors | 1.30 cfm/sf | 1.30 cfm/sf | 1.3 cfm/sf |  | 1.3 cfm/sf |  | 1.3 cfm/sf
Rooms containing fuel-burning appliances
|  |  | Ducted combustion air for space conditioning appliances | Appliances and openings located outside thermal envelope or | Appliances and openings located outside thermal envelope or | Appliances and openings located outside thermal envelope or
|  |  |  | Enclosed in room isolated from inside thermal envelope and with ≥R-8 insulation on combustion air duct in conditioned space | In enclosed, isolated & insulated room inside thermal envelope and with ≥R-8 insulation on combustion air duct in conditioned space | In enclosed, isolated & insulated room inside thermal envelope and with ≥R-8 insulation on combustion air duct in conditioned space
Doors and access openings to shafts, chutes, stairways and elevator lobbies
|  |  | From conditioned space | Meet air infiltration requirements if in thermal envelope | Meet air infiltration requirements if in thermal envelope | Meet air infiltration requirements if in thermal envelope
|  |  | Not in thermal envelope from conditioned space | Be gasketed, weatherstripped or sealed | Be gasketed, weatherstripped or sealed | Be gasketed, weatherstripped or sealed
|  | Air intakes, exhaust openings, stairways and shafts integral to building envelope |  | Provided with dampers | Provided with dampers | Provided with dampers |  | Provided with dampers |  | Provided with dampers
|  |  | Stairway and shaft vents | Motorized dampers with maximum leakage rate of 4 cfm/sf | Motorized dampers with maximum leakage rate of 4 cfm/sf | Motorized dampers with maximum leakage rate of 4 cfm/sf |  | Motorized dampers with maximum leakage rate of 4 cfm/sf |  | Motorized dampers with maximum leakage rate of 4 cfm/sf
|  |  | Outdoor air intakes and exhausts | Motorized dampers with maximum leakage rate of 4 cfm/sf | Motorized dampers with maximum leakage rate of 4 cfm/sf | Motorized dampers with maximum leakage rate of 4 cfm/sf |  | Motorized dampers with maximum leakage rate of 4 cfm/sf |  | Motorized dampers with maximum leakage rate of 4 cfm/sf
|  |  |  | Gravity dampers for defined exceptions | Gravity dampers for defined exceptions | Gravity dampers for defined exceptions |  | Gravity exhaust dampers with maximum leakage rate of 20 cfm/sf allowed in buildings <3 stories |  | Gravity dampers with maximum leakage rate of 20 cfm/sf allowed on air intakes or exhaust capacity ≤300 cfm
|  | Loading dock weatherseals |  | Yes | Yes | Yes |  | Yes |  | Yes
|  | Building entrance vestibules with self-closing device on doors |  | Space ≥3000 sf without revolving door or air curtain | Space ≥3000 sf without revolving door or air curtain | From space ≥3000 sf without revolving door or air curtain |  | Vestibule floor area ≤50 sf or 2% of gross conditioned floor area of that level |  | Vestibule floor area ≤50 sf or 2% of gross conditioned floor area of that level
Continuous air barrier on exterior surfaces of both conditioned and unconditioned vestibules
[8 empty] | Exterior envelope of conditioned vestibule meet requirements for conditioned space |  | Exterior envelope of conditioned vestibule meet requirements for conditioned space
[8 empty] | Interior & exterior envelope of unconditioned vestibule meet requirements for semiheated space |  | Interior & exterior envelope of unconditioned vestibule meet requirements for semiheated space
[8 empty] | Building entrance from space ≥1,000 sf without revolving door |  | Building gross conditioned floor area ≥1,000 sf
[8 empty] | Doors opening directly from space ≥3,000 sf and is not separated from building entrance |  | Doors opening directly from space ≥3,000 sf and is not separated from building entrance
|  | Recessed lighting In thermal envelope |  | IC-Rated | IC-Rated | IC-Rated |  | Not recessed in manner as to affect insulation thickness |  | Not recessed in manner as to affect insulation thickness
|  |  |  | Labeled air leakage rate ≤2.0 cfm | Labeled air leakage rate ≤2.0 cfm | Labeled air leakage rate ≤2.0 cfm |  | Comply with envelope air leakage requirements |  | Comply with envelope air leakage requirements
|  |  |  | Sealed with gasket or caulk between housing and interior covering | Sealed with gasket or caulk between housing and interior covering | Sealed with gasket or caulk between housing and interior covering
|  | Operable openings interlocking |  |  |  | Operable openings to outdoors >40 sf interlocked with heating and cooling system so as to |  | Doors opening to outdoors interlocked with heating and cooling system so as to |  | Doors opening to outdoors interlocked with heating and cooling system so as to
[6 empty] | Raise cooling setpoint to 90℉ |  | Raise cooling setpoint to 90℉ |  | Raise cooling setpoint to 90℉
[6 empty] | Lower heating setpoint to 55℉ |  | Lower heating setpoint to 55℉ |  | Lower heating setpoint to 55℉
[6 empty] | Within 10 minutes of opening operable opening |  | Within 5 minutes of opening operable opening |  | Within 5 minutes of opening operable opening
Heating, Ventilating and Air Conditioning
| Simplified Approach (ASHRAE), Simple Systems (IECC) | [6 empty] | ≤2 stories and ≤25,000 sf with compliant single zone HVAC system |  | ≤2 stories and ≤25,000 sf with compliant single zone HVAC system
[8 empty] | Has defined criteria and requirements |  | Has defined criteria and requirements
| Equipment and System Sizing |  |  | Use Standard 183 for heating and cooling system design load calculations | Use Standard 183 for heating and cooling system design load calculations | Use Standard 183 for heating and cooling system design load calculations |  | Use Standard 183 for heating and cooling system design load calculations |  | Use Standard 183 for heating and cooling system design load calculations
|  |  |  | Loads adjusted to account for energy recovery | Loads adjusted to account for energy recovery | Loads adjusted to account for energy recovery |  | Calculate pressure drop through each device and pipe segment in critical circuit at design conditions |  | Calculate pressure drop through each device and pipe segment in critical circuit at design conditions
|  |  |  | Heating & cooling equipment capacity ≤ calculated loads | Heating & cooling capacity ≤ smallest available equipment size that exceeds calculated loads | Heating & cooling capacity ≤ smallest available equipment size that exceeds calculated loads
[6 empty] | Data Centers |  | Alternate Compliance Path for |  | Alternate Compliance Path for
[8 empty] | Computer room systems |  | Computer room systems
[6 empty] | Comply with Sections 6 & 8 of ASHRAE 90.4 with following changes |  | HVAC systems serving heating, cooling or ventilating needs of computer room may comply with: |  | HVAC systems serving heating, cooling or ventilating needs of computer room with ≥10 kW IT equipment load shall comply with ASHRAE Standard 90.4, Energy Standard for Data Centers
[6 empty] | Replace design mechanical load component (MLC) with 0.22 for Climate Zone 5A |  | Computer room PUE1 ≤1.36
[6 empty] | Replace annualized mechanical load component (MLC) with 0.17 for Climate Zone 5A |  | Highest value computer room PUE0 ≤1.36 where PEU0 calculated at 100% design IT equipment energy use and 50% design IT equipment energy
Provide documentation
Fault Detection and Diagnostics
|  |  | Where required |  |  | New buildings with HVAC system serving gross conditioned floor area ≥100,000 sf
|  |  | Monitor HVAC system's performance & automatically identify faults |  |  | Include permanently installed sensors & devices
Sample performance at least once every 15 minutes
Automatically identify and report faults
Automatically notify authorized personnel
Automatically provide prioritized recommendations for repair based on analysis of data collected
Capable of transmitting prioritized fault repair recommendations to remotely located authorized personnel
Ceiling Fans
|  | Large-diameter ceiling fans |  |  |  | Rated with AMCA 230 |  |  |  | Rated with 10 CFR 430 Appendix U or AMCA 230
based on blade span, rated airflow and power consumption at maximum speed
Mechanical Equipment Efficiency
| Air Conditioners, Air Cooled |  |  |  |  | Before 1/1/2023 | After 1/1/2023 |  |  | Before 1/1/2023 | After 1/1/2023
|  | <65,000 Btu/h, split systems |  | 13.0 SEER | 13.0 SEER | 13.0 SEER | 13.4 SEER2 | 13.0 SEER |  | 13.0 SEER | 13.4 SEER2
|  | <65,000 Btu/h, single package |  | 14.0 SEER | 14.0 SEER | 14.0 SEER | 13.4 SEER2 | 14.0 SEER |  | 14.0 SEER | 13.4 SEER2
|  | ≤30,000 Btu/h Through-the-wall (space constrained), air cooled, split system |  | 12.0 SEER | 12.0 SEER | 12.0 SEER | 11.7 SEER2 | 12.0 SEER |  | 12.0 SEER | 11.7 SEER2
|  | ≤30,000 Btu/h Through-the-wall air cooled single package |  | 12.0 SEER | 12.0 SEER | 12.0 SEER | 11.7 SEER2 | 12.0 SEER |  | 12.0 SEER | 11.7 SEER2
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.2 EER 12.8 IEER | 11.2 EER 12.8 IEER | 11.2 EER 12.9 IEER | 11.2 EER 14.8 IEER | 11.2 EER 12.9 IEER |  | 11.2 EER 12.9 IEER | 11.2 EER 14.8 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 11.0 EER 12.6 IEER | 11.0 EER 12.6 IEER | 11.0 EER 12.7 IEER | 11.0 EER 14.6 IEER | 11.0 EER 12.7 IEER |  | 11.0 EER 12.7 IEER | 11.0 EER 14.6 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.0 EER 12.4 IEER | 11.0 EER 12.4 IEER | 11.0 EER 12.4 IEER | 11.0 EER 14.2 IEER | 11.0 EER 12.4 IEER |  | 11.0 EER 12.4 IEER | 11.0 EER 14.2 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 10.8 EER 12.2 IEER | 10.8 EER 12.2 IEER | 10.8 EER 12.2 IEER | 10.8 EER 14.0 IEER | 10.8 EER 12.2 IEER |  | 10.8 EER 12.2 IEER | 10.8 EER 14.0 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 10.0 EER 11.6 IEER | 10.0 EER 11.6 IEER | 10.0 EER 11.6 IEER | 10.0 EER 13.2 IEER | 10.0 EER 11.6 IEER |  | 10.0 EER 11.6 IEER | 10.0 EER 13.2 IEER
|  | ≥240,000 & <760,000 Btu/h, All other heating section, split system and single package |  | 9.8 EER 11.4 IEER | 9.8 EER 11.4 IEER | 9.8 EER 11.4 IEER | 9.8 EER 13.0 IEER | 9.8 EER 11.4 IEER |  | 9.8 EER 11.4 IEER | 9.8 EER 13.0 IEER
|  | ≥760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 9.7 EER 11.2 IEER | 9.7 EER 11.2 IEER | 9.7 EER 11.2 IEER | 9.7 EER 12.5 IEER | 9.7 EER 11.2 IEER |  | 9.7 EER 11.2 IEER | 9.7 EER 12.5 IEER
|  | ≥760,000 Btu/h, All other heating section, split system and single package |  | 9.5 EER 11.0 IEER | 9.5 EER 11.0 IEER | 9.5 EER 11.0 IEER | 9.5 EER 12.3 IEER | 9.5 EER 11.0 IEER |  | 9.5 EER 11.0 IEER | 9.5 EER 12.3 IEER
|  | <65,000 Btu/h Small-duct high-velocity, air cooled split system |  | 11.0 SEER | 11.0 SEER | 12.0 SEER | 12.1 SEER2 | 11.0 SEER |  | 12.0 SEER | 12.0 SEER2
Air Conditioner, Water Cooled
|  | <65,000 Btu/h, Split systems and single package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER |  | 12.1 EER 12.3 IEER |  | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.1 EER 13.9 IEER | 12.1 EER 13.9 IEER | 12.1 EER 13.9 IEER |  | 12.1 EER 13.9 IEER |  | 12.1 EER 13.9 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 11.9 EER 13.7 IEER | 11.9 EER 13.7 IEER | 11.9 EER 13.7 IEER |  | 11.9 EER 13.7 IEER |  | 11.9 EER 13.7 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.5 EER 13.9 IEER | 12.5 EER 13.9 IEER | 12.5 EER 13.9 IEER |  | 12.5 EER 13.9 IEER |  | 12.5 EER 13.9 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 12.3 EER 13.7 IEER | 12.3 EER 13.7 IEER | 12.3 EER 13.7 IEER |  | 12.3 EER 13.7 IEER |  | 12.3 EER 13.7 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.4 EER 13.6 IEER | 12.4 EER 13.6 IEER | 12.4 EER 13.6 IEER |  | 12.4 EER 13.6 IEER |  | 12.4 EER 13.6 IEER
|  | ≥240,000 & <760,000 Btu/h, All other heating section, split system and single package |  | 12.2 EER 13.4 IEER | 12.2 EER 13.4 IEER | 12.2 EER 13.4 IEER |  | 12.2 EER 13.4 IEER |  | 12.2 EER 13.4 IEER
|  | ≥760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.2 EER 13.5 IEER | 12.2 EER 13.5 IEER | 12.2 EER 13.5 IEER |  | 12.2 EER 13.5 IEER |  | 12.2 EER 13.5 IEER
|  | ≥760,000 Btu/h, All other heating section, split system and single package |  | 12.0 EER 13.3 IEER | 12.0 EER 13.3 IEER | 12.0 EER 13.3 IEER |  | 12.0 EER 13.3 IEER |  | 12.0 EER 13.3 IEER
Air Conditioner, Evaporatively Cooled
|  | <65,000 Btu/h, Split systems and single package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER |  | 12.1 EER 12.3 IEER |  | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER |  | 12.1 EER 12.3 IEER |  | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER |  | 11.9 EER 12.1 IEER |  | 11.9 EER 12.1 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.0 EER 12.2 IEER | 12.0 EER 12.2 IEER | 12.0 EER 12.2 IEER |  | 11.9 EER 12.1 IEER |  | 12.0 EER 12.2 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 11.8 EER 12.0 IEER | 11.8 EER 12.0 IEER | 11.8 EER 12.0 IEER |  | 11.8 EER 12.0 IEER |  | 11.8 EER 12.0 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER |  | 11.9 EER 12.1 IEER |  | 11.9 EER 12.1 IEER
|  | ≥240,000 & <760,000 Btu/h, All other heating section, split system and single package |  | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER |  | 11.7 EER 11.9 IEER |  | 11.7 EER 11.9 IEER
|  | ≥760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER |  | 11.7 EER 11.9 IEER |  | 11.7 EER 11.9 IEER
|  | ≥760,000 Btu/h, All other heating section, split system and single package |  | 11.5 EER 11.7 IEER | 11.5 EER 11.7 IEER | 11.5 EER 11.7 IEER |  | 11.5 EER 11.7 IEER |  | 11.5 EER 11.7 IEER
Condensing Units, Air Cooled
|  |  | ≥135,000 Btu/h | 10.5 EER 11.8 IPLV | 10.5 EER 11.8 IPLV | 10.5 EER 11.8 IEER |  | 10.5 EER 11.8 IEER |  | 10.5 EER 11.8 IEER
Condensing Units, Water Cooled
|  |  | ≥135,000 Btu/h | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IEER |  | 13.5 EER 14.0 IEER |  | 13.5 EER 14.0 IEER
Condensing Units, Evaporatively Cooled
|  |  | ≥135,000 Btu/h | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IEER |  | 13.5 EER 14.0 IEER |  | 13.5 EER 14.0 IEER
| Heat Pumps, Electrically Operated, Air Cooled (Cooling Mode) |  |  |  |  | Before 1/1/2023 | After 1/1/2023 |  |  | Before 1/1/2023 | After 1/1/2023
|  | <65,000 Btu/h, Split systems |  | 14.0 SEER | 14.0 SEER | 14.0 SEER | 14.3 SEER2 | 14.0 SEER |  | 14.0 SEER | 14.3 SEER2
|  | <65,000 Btu/h, Single package |  | 14.0 SEER | 14.0 SEER | 14.0 SEER | 13.4 SEER2 | 14.0 SEER |  | 14.0 SEER | 13.4 SEER2
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.0 EER 12.0 IEER | 11.0 EER 12.0 IEER | 11.0 EER 12.2 IEER | 11.0 EER 14.1 IEER | 11.0 EER 12.2 IEER |  | 11.0 EER 12.2 IEER | 11.0 EER 14.1 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 10.8 EER 11.8 IEER | 10.8 EER 11.8 IEER | 10.8 EER 12.0 IEER | 10.8 EER 13.9 IEER | 10.8 EER 12.0 IEER |  | 10.8 EER 12.0 IEER | 10.8 EER 13.9 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 10.6 EER 11.6 IEER | 10.6 EER 11.6 IEER | 10.6 EER 11.6 IEER | 10.6 EER 13.5 IEER | 10.6 EER 11.6 IEER |  | 10.6 EER 11.6 IEER | 10.6 EER 13.5 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 10.4 EER 11.4 IEER | 10.4 EER 11.4 IEER | 10.4 EER 11.4 IEER | 10.4 EER 13.3 IEER | 10.4 EER 11.4 IEER |  | 10.4 EER 11.4 IEER | 10.4 EER 13.3 IEER
|  | ≥240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 9.5 EER 10.6 IEER | 9.5 EER 10.6 IEER | 9.5 EER 10.6 IEER | 9.5 EER 12.5 IEER | 9.5 EER 10.6 IEER |  | 9.5 EER 10.6 IEER | 9.5 EER 12.5 IEER
|  | ≥240,000 Btu/h, All other heating section, split system and single package |  | 9.3 EER 9.4 IEER | 9.3 EER 9.4 IEER | 9.3 EER 10.4 IEER | 9.3 EER 12.3 IEER | 9.3 EER 9.4 IEER |  | 9.3 EER 10.4 IEER | 9.3 EER 12.3 IEER
|  | ≤30,000 Btu/h Through-the-wall (space constrained), air cooled split system |  | 12.0 SEER | 12.0 SEER | 12.0 SEER | 11.7 SEER2 | 12.0 SEER |  | 12.0 SEER | 11.7 SEER2
|  | ≤30,000 Btu/h Through-the-wall, air cooled, single package |  | 12.0 SEER | 12.0 SEER | 12.0 SEER | 11.7 SEER2 | 12.0 SEER |  | 12.0 SEER | 11.7 SEER2
|  | <65,000 Btu/h Small-duct high velocity, split system |  | 11.0 SEER | 11.0 SEER | 12.0 SEER | 12.0 SEER2 | 11.0 SEER |  | 12.0 SEER | 12.0 SEER2
Heat Pumps, Electrically Operated, Water to Air, 86℉ Entering Water (Cooling Mode)
|  |  | <17,000 Btu/h | 12.2 EER | 12.2 EER | 12.2 EER |  | 12.2 EER |  | 12.2 EER
|  |  | ≥17,000 & <65,000 Btu/h | 13.0 EER | 13.0 EER | 13.0 EER |  | 13.0 EER |  | 13.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 13.0 EER | 13.0 EER | 13.0 EER |  | 13.0 EER |  | 13.0 EER
Heat Pumps, Electrically Operated, Water to Air, Groundwater Source, 59ºF Entering Water (Cooling Mode)
|  |  | <135,000 Btu/h | 18.0 EER | 18.0 EER | 18.0 EER |  | 18.0 EER |  | 18.0 EER
Heat Pumps, Electrically Operated, Brine to Air, Ground Loop, 77ºF Entering Water (Cooling Mode)
|  |  | <135,000 Btu/h | 14.1 EER | 14.1 EER | 14.1 EER |  | 14.1 EER |  | 14.1 EER
Heat Pumps, Electrically Operated, Water to Water, Water (loop) Source, (Cooling Mode)
|  | <135,000 Btu/h, 86° entering water temperature |  | 10.6 EER | 10.6 EER | 10.6 EER |  | 10.6 EER |  | 10.6 EER
|  | <135,000 Btu/h, 59° entering water temperature |  | 16.3 EER | 16.3 EER | 16.3 EER |  | 16.3 EER |  | 16.3 EER
Heat Pumps, Electrically Operated, Brine to Water, Ground Loop, 77ºF Entering Water (Cooling Mode)
|  |  | <135,000 Btu/h | 12.1 EER | 12.1 EER | 12.1 EER |  | 12.1 EER |  | 12.1 EER
| Heat Pumps, Electrically Operated, Air Cooled (Heating Mode) |  |  |  |  | Before 1/1/2023 | After 1/1/2023 |  |  | Before 1/1/2023 | After 1/1/2023
|  | <65,000 Btu/h (cooling capacity), split systems |  | 8.2 HSPF | 8.2 HSPF | 8.2 HSPF | 7.5 HSPF2 | 8.2 HSPF |  | 8.2 HSPF | 7.5 HSPF2
|  | <65,000 Btu/h (cooling capacity), single package |  | 8.0 HSPF | 8.0 HSPF | 8.0 HSPF | 6.7 HSPF2 | 8.0 HSPF |  | 8.0 HSPF | 6.7 HSPF2
|  | ≥65,000 & <135,000 Btu/h (cooling capacity), 47ºF db/43ºF wb outdoor air |  | 3.3 COP | 3.3 COP | 3.3 COPH | 3.4 COPH | 3.3 COPH |  | 3.3 COPH | 3.4 COPH
|  | ≥65,000 & <135,000 Btu/h (cooling capacity), 17ºF db/15ºF wb outdoor air |  | 2.25 COP | 2.25 COP | 2.25 COPH | 2.25 COPH | 2.25 COPH |  | 2.25 COPH | 2.25 COPH
|  | ≥135,000 & <240,000 Btu/h (cooling capacity), 47ºF db/43ºF wb outdoor air |  | 3.2 COP | 3.2 COP | 3.2 COPH | 3.3 COPH | 3.2 COPH |  | 3.2 COPH | 3.3 COPH
|  | ≥135,000 & <240,000 Btu/h (cooling capacity), 17ºF db/15ºF wb outdoor air |  | 2.05 COP | 2.05 COP | 2.05 COPH | 2.05 COPH | 2.05 COPH |  | 2.05 COPH | 2.05 COPH
|  | ≥240,000 Btu/h (cooling capacity), 47ºF db/43ºF wb outdoor air |  |  | 3.2 COP | 3.2 COPH | 3.2 COPH | 3.2 COPH |  | 3.2 COPH | 3.2 COPH
|  | ≥240,000 Btu/h (cooling capacity), 17ºF db/15ºF wb outdoor air |  |  | 2.05 COP | 2.05 COPH | 2.05 COPH | 2.05 COPH |  | 2.05 COPH | 2.05 COPH
|  | ≤30,000 Btu/h Through-the-Wall (space constrained), split system |  | 7.4 HSPF | 7.4 HSPF | 7.4 HSPF | 6.3 HSPF2 | 7.4 HSPF |  | 7.4 HSPF | 6.3 HSPF2
|  | ≤30,000 Btu/h Through-the-Wall (space constrained), single package |  | 7.4 HSPF | 7.4 HSPF | 7.4 HSPF | 6.3 HSPF2 | 7.4 HSPF |  | 7.4 HSPF | 6.3 HSPF2
|  | <65,000 Btu/h Small-duct high velocity, split system |  | 6.8 HSPF | 6.8 HSPF | 7.2 HSPF | 6.1 HSPF2 | 6.8 HSPF |  | 7.2 HSPF | 6.1 HSPF2
Heat Pumps, Electrically Operated, Water to Air, Water Loop, 68℉ Entering Water (Heating Mode)
|  | <135,000 Btu/h (cooling capacity) |  | 4.3 COP | 4.3 COP | 4.3 COPH |  | 4.3 COP |  | 4.3 COPH
Heat Pumps, Electrically Operated, Water to Air, Groundwater Loop, 50ºF Entering Water (Heating Mode)
|  | <135,000 Btu/h (cooling capacity) |  | 3.7 COP | 3.7 COP | 3.7 COPH |  | 3.7 COP |  | 3.7 COPH
Heat Pumps, Electrically Operated, Water (Brine) to Air, Ground Loop, 32ºF Entering Water (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 3.2 COP | 3.2 COP | 3.2 COPH |  | 3.2 COP |  | 3.2 COPH
Heat Pumps, Electrically Operated, Water to Water, Water Loop, 68º Entering Water (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 3.7 COP | 3.7 COP | 3.7 COPH |  | 3.7 COP |  | 3.7 COPH
Heat Pumps, Electrically Operated, Water to Water, Ground Water, 50º Entering Water (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 3.1 COP | 3.1 COP | 3.1 COPH |  | 3.1 COP |  | 3.1 COPH
Heat Pumps, Electrically Operated, Brine to Water, Ground Loop, 32º Entering Fluid (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 2.5 COP | 2.5 COP | 2.5 COPH |  | 2.5 COP |  | 2.5 COPH
Condensing Units, Air Cooled
|  |  | ≥135,000 Btu/h | 10.1 EER 11.2 IPLV | 10.1 EER 11.2 IPLV | 10.5 EER 11.8 IEER |  | 10.5 EER 11.8 IEER |  | 10.5 EER 11.8 IEER
Condensing Units, Water or Evaporatively Cooled
|  |  | ≥135,000 Btu/h | 13.1 EER 13.1 IPLV | 13.1 EER 13.1 IPLV | 13.5 EER 14.0 IEER |  | 13.5 EER 14.0 IEER |  | 13.5 EER 14.0 IEER
Electrically Operated Package Terminal and Single Package Vertical Air Conditioners & Heat Pumps
|  | PTAC (cooling mode) new construction (standard size in 90.1) |  | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER |  |  | 14.0 - (0.300 x Cap/1000) EER
|  |  | <7,000 Btu/h |  |  | 11.9 EER |  |  |  | 11.9 EER
|  |  | ≥7,000 & ≤15,000 Btu/h |  |  | 14.0 - (0.300 x Cap/1000) EER |  |  |  | 14.0 - (0.300 x Cap/1000) EER
|  |  | >15,000 Btu/h |  |  | 9.5 EER |  |  |  | 9.5 EER
|  | PTAC (cooling mode) replacement (nonstandard size in 90.1) |  | 10.9 - (0.213 x Cap/1000) EER | 10.9 - (0.213 x Cap/1000) EER |  |  | 10.9 - (0.213 x Cap/1000) EER
|  |  | <7,000 Btu/h |  |  | 9.4 EER |  |  |  | 9.4 EER
|  |  | ≥7,000 & ≤15,000 Btu/h |  |  | 10.9 - (0.213 x Cap/1000) EER |  |  |  | 10.9 - (0.213 x Cap/1000) EER
|  |  | >15,000 Btu/h |  |  | 7.7 EER |  |  |  | 7.7 EER
|  | PTHP (cooling mode) new construction (standard size in 90.1) |  | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER |  |  | 14.0 - (0.300 x Cap/1000) EER
|  |  | <7,000 Btu/h |  |  | 11.9 EER |  |  |  | 11.9 EER
|  |  | ≥7,000 & ≤15,000 Btu/h |  |  | 14.0 - (0.300 x Cap/1000) EER |  |  |  | 14.0 - (0.300 x Cap/1000) EER
|  |  | >15,000 Btu/h |  |  | 9.5 EER |  |  |  | 9.5 EER
|  | PTHP (cooling mode) replacement (nonstandard size in 90.1) |  | 10.8 - (0.213 x Cap/1000) EER | 10.8 - (0.213 x Cap/1000) EER |  |  | 10.8 - (0.213 x Cap/1000) EER
|  |  | <7,000 Btu/h |  |  | 9.3 EER |  |  |  | 9.3 EER
|  |  | ≥7,000 & ≤15,000 Btu/h |  |  | 10.8 - (0.213 x Cap/1000) EER |  |  |  | 10.8 - (0.213 x Cap/1000) EER
|  |  | >15,000 Btu/h |  |  | 7.6 EER |  |  |  | 7.6 EER
|  | PTHP (heating mode) new construction (standard size in 90.1) |  | 3.2 - (0.026 x Cap/1000) COP | 3.2 - (0.026 x Cap/1000) COP |  |  | 3.7 - (0.052 x Cap/1000) COPH
|  |  | <7,000 Btu/h |  |  | 3.3 COPH |  |  |  | 3.3 COPH
|  |  | ≥7,000 & ≤15,000 Btu/h |  |  | 3.7 - (0.052 x Cap/1000) COPH |  |  |  | 3.7 - (0.052 x Cap/1000) COPH
|  |  | >15,000 Btu/h |  |  | 2.9 COPH |  |  |  | 2.9 COPH
|  | PTHP (heating mode) replacement (nonstandard size in 90.1) |  | 2.9 - (0.026 x Cap/1000) COP | 2.9 - (0.026 x Cap/1000) COP |  |  | 2.9 - (0.026 x Cap/1000) COPH
|  |  | <7,000 Btu/h |  |  | 2.7 COPH |  |  |  | 2.7 COPH
|  |  | ≥7,000 & ≤15,000 Btu/h |  |  | 2.9 - (0.026 x Cap/1000) COPH |  |  |  | 2.9 - (0.026 x Cap/1000) COPH
|  |  | >15,000 Btu/h |  |  | 2.5 COPH |  |  |  | 2.5 COPH
SPVAC (cooling mode)
|  |  | <65,000 Btu/h | 9.0 EER | 9.0 EER | 11.0 EER |  | 10.0 EER |  | 11.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 8.9 EER | 8.9 EER | 10.0 EER |  | 10.0 EER |  | 10.0 EER
|  |  | ≥135,000 & <240,000 Btu/h | 8.6 EER | 8.6 EER | 10.0 EER |  | 10.0 EER |  | 10.0 EER
SPVHP (cooling mode)
|  |  | <65,000 Btu/h | 9.0 EER | 9.0 EER | 11.0 EER |  | 10.0 EER |  | 11.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 8.9 EER | 8.9 EER | 10.0 EER |  | 10.0 EER |  | 10.0 EER
|  |  | ≥135,000 & <240,000 Btu/h | 8.6 EER | 8.6 EER | 10.1 EER |  | 10.0 EER |  | 10.0 EER
SPVHP (heating mode)
|  |  | <65,000 Btu/h | 3.0 COP | 3.0 COP | 3.3 COPH |  | 3.0 COPH |  | 3.3 COPH
|  |  | ≥65,000 & <135,000 Btu/h | 3.0 COP | 3.0 COP | 3.0 COPH |  | 3.0 COPH |  | 3.0 COPH
|  |  | ≥135,000 & <240,000 Btu/h | 2.9 COP | 2.9 COP | 3.0 COPH |  | 3.0 COPH |  | 3.0 COPH
SPVAC (cooling mode), nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  |  |  |  | 9.2 EER
|  |  | >30,000 and ≤36,000 Btu/h |  |  |  |  | 9.0 EER
SPVHP (heating mode) nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  |  |  |  | 3.0 COPH
|  |  | >30,000 and ≤36,000 Btu/h |  |  |  |  | 3.0 COPH
Heat-Pump & Heat Recovery Chiller Packages
Air source
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 47 db / 43 wb OAT |  |  | ≥9.595 FL ≥13.02 IPLV | ≥9.215 FL ≥15.01 IPLV |  |  | ≥9.595 FL ≥13.02 IPLV | ≥9.215 FL ≥15.01 IPLV
|  |  | 17 db / 15 db OAT |  |  | ≥9.595 FL ≥13.30 IPLV | ≥9.215 FL ≥15.30 IPLV |  |  | ≥9.595 FL ≥13.30 IPLV | ≥9.215 FL ≥15.30 IPLV
Heat-pump heating, 47 db / 43 wb OAT
|  |  | Low - 105℉ LWT |  |  | ≥3.290 |  |  |  | ≥3.290
|  |  | Medium - 120℉ LWT |  |  | ≥2.770 |  |  |  | ≥2.770
|  |  | High - 140℉ LWT |  |  | ≥2.310 |  |  |  | ≥2.310
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 17 db / 15 wb OAT
|  |  | Low - 105℉ LWT |  |  | ≥2.230 |  |  |  | ≥2.230
|  |  | Medium - 120℉ LWT |  |  | ≥1.950 |  |  |  | ≥1.950
|  |  | High - 140℉ LWT |  |  | ≥1.630 |  |  |  | ≥1.630
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Heat recovery chiller heating |  |  | NA |  |  |  | NA
Water source, positive displacement <75 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.7885 FL ≤0.6316 IPLV | ≤0.7875 FL ≤0.5145 IPLV |  |  | ≤0.7885 FL ≤0.6316 IPLV | ≤0.7875 FL ≤0.5145 IPLV
|  |  | 75/65 WT |  |  | ≤0.7885 FL ≤0.6316 IPLV | ≤0.7875 FL ≤0.5145 IPLV |  |  | ≤0.7885 FL ≤0.6316 IPLV | ≤0.7875 FL ≤0.5145 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.64 |  |  |  | ≥4.64
|  |  | Medium - 120℉ LWT |  |  | ≥3.680 |  |  |  | ≥3.680
|  |  | High - 140℉ LWT |  |  | ≥2.680 |  |  |  | ≥2.680
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.550 |  |  |  | ≥3.550
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.330 |  |  |  | ≥8.330
|  |  | Medium - 120℉ LWT |  |  | ≥6.410 |  |  |  | ≥6.410
|  |  | High - 140℉ LWT |  |  | ≥4.420 |  |  |  | ≥4.420
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | 6.15 |  |  |  | 6.15
Water source, positive displacement ≥75 & <150 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.7579 FL ≤0.5895 IPLV | ≤0.7140 FL ≤0.4620 IPLV |  |  | ≤0.7579 FL ≤0.5895 IPLV | ≤0.7140 FL ≤0.4620 IPLV
|  |  | 75/65 WT |  |  | ≤0.7579 FL ≤0.5895 IPLV | ≤0.7140 FL ≤0.4620 IPLV |  |  | ≤0.7579 FL ≤0.5895 IPLV | ≤0.7140 FL ≤0.4620 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.640 |  |  |  | ≥4.640
|  |  | Medium - 120℉ LWT |  |  | ≥3.680 |  |  |  | ≥3.680
|  |  | High - 140℉ LWT |  |  | ≥2.680 |  |  |  | ≥2.680
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.550 |  |  |  | ≥3.550
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.330 |  |  |  | ≥8.330
|  |  | Medium - 120℉ LWT |  |  | ≥6.410 |  |  |  | ≥6.410
|  |  | High - 140℉ LWT |  |  | ≥4.420 |  |  |  | ≥4.420
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | 6.15 |  |  |  | 6.15
Water source, positive displacement ≥150 & < 300 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.6947 FL ≤0.5684 IPLV | ≤0.7140 FL ≤0.4620 IPLV |  |  | ≤0.6947 FL ≤0.5684 IPLV | ≤0.7140 FL ≤0.4620 IPLV
|  |  | 75/65 WT |  |  | ≤0.6947 FL ≤0.5684 IPLV | ≤0.7140 FL ≤0.4620 IPLV |  |  | ≤0.6947 FL ≤0.5684 IPLV | ≤0.7140 FL ≤0.4620 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.640 |  |  |  | ≥4.640
|  |  | Medium - 120℉ LWT |  |  | ≥3.680 |  |  |  | ≥3.680
|  |  | High - 140℉ LWT |  |  | ≥2.680 |  |  |  | ≥2.680
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.550 |  |  |  | ≥3.550
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.330 |  |  |  | ≥8.330
|  |  | Medium - 120℉ LWT |  |  | ≥6.410 |  |  |  | ≥6.410
|  |  | High - 140℉ LWT |  |  | ≥4.420 |  |  |  | ≥4.420
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | 6.15 |  |  |  | 6.15
Water source, positive displacement ≥300 & <600 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.6421 FL ≤0.5474 IPLV | ≤0.6563 FL ≤0.4305 IPLV |  |  | ≤0.6421 FL ≤0.5474 IPLV | ≤0.6563 FL ≤0.4305 IPLV
|  |  | 75/65 WT |  |  | ≤0.6421 FL ≤0.5474 IPLV | ≤0.6563 FL ≤0.4305 IPLV |  |  | ≤0.6421 FL ≤0.5474 IPLV | ≤0.6563 FL ≤0.4305 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.930 |  |  |  | ≥4.930
|  |  | Medium - 120℉ LWT |  |  | ≥3.960 |  |  |  | ≥3.960
|  |  | High - 140℉ LWT |  |  | ≥2.970 |  |  |  | ≥2.970
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.900 |  |  |  | ≥3.900
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.900 |  |  |  | ≥8.900
|  |  | Medium - 120℉ LWT |  |  | ≥6.980 |  |  |  | ≥6.980
|  |  | High - 140℉ LWT |  |  | ≥5.000 |  |  |  | ≥5.000
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | 6.85 |  |  |  | 6.85
Water source, positive displacement ≥600 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6143 FL ≤0.3990 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6143 FL ≤0.3990 IPLV
|  |  | 75/65 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6143 FL ≤0.3990 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6143 FL ≤0.3990 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.930 |  |  |  | ≥4.930
|  |  | Medium - 120℉ LWT |  |  | ≥3.960 |  |  |  | ≥3.960
|  |  | High - 140℉ LWT |  |  | ≥2.970 |  |  |  | ≥2.970
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.900 |  |  |  | ≥3.900
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.900 |  |  |  | ≥8.900
|  |  | Medium - 120℉ LWT |  |  | ≥6.980 |  |  |  | ≥6.980
|  |  | High - 140℉ LWT |  |  | ≥5.000 |  |  |  | ≥5.000
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | 6.85 |  |  |  | 6.85
Water source, centrifugal <75 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.6421 FL ≤0.5789 IPLV | ≤0.7316 FL ≤0.4632 IPLV |  |  | ≤0.6421 FL ≤0.5789 IPLV | ≤0.7316 FL ≤0.4632 IPLV
|  |  | 75/65 WT |  |  | ≤0.6421 FL ≤0.5789 IPLV | ≤0.7316 FL ≤0.4632 IPLV |  |  | ≤0.6421 FL ≤0.5789 IPLV | ≤0.7316 FL ≤0.4632 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.640 |  |  |  | ≥4.640
|  |  | Medium - 120℉ LWT |  |  | ≥3.680 |  |  |  | ≥3.680
|  |  | High - 140℉ LWT |  |  | ≥2.680 |  |  |  | ≥2.680
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.550 |  |  |  | ≥3.550
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.330 |  |  |  | ≥8.330
|  |  | Medium - 120℉ LWT |  |  | ≥6.410 |  |  |  | ≥6.410
|  |  | High - 140℉ LWT |  |  | ≥4.420 |  |  |  | ≥4.420
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥6.150 |  |  |  | ≥6.150
Water source, centrifugal ≥75 & <150 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.5895 FL ≤0.5474 IPLV | ≤0.6684 FL ≤0.4211 IPLV |  |  | ≤0.5895 FL ≤0.5474 IPLV | ≤0.6684 FL ≤0.4211 IPLV
|  |  | 75/65 WT |  |  | ≤0.5895 FL ≤0.5474 IPLV | ≤0.6684 FL ≤0.4211 IPLV |  |  | ≤0.5895 FL ≤0.5474 IPLV | ≤0.6684 FL ≤0.4211 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.640 |  |  |  | ≥4.640
|  |  | Medium - 120℉ LWT |  |  | ≥3.680 |  |  |  | ≥3.680
|  |  | High - 140℉ LWT |  |  | ≥2.680 |  |  |  | ≥2.680
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.550 |  |  |  | ≥3.550
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.330 |  |  |  | ≥8.330
|  |  | Medium - 120℉ LWT |  |  | ≥6.410 |  |  |  | ≥6.410
|  |  | High - 140℉ LWT |  |  | ≥4.420 |  |  |  | ≥4.420
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥6.150 |  |  |  | ≥6.150
Water source, centrifugal ≥150 & < 300 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6263 FL ≤0.4105 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6263 FL ≤0.4105 IPLV
|  |  | 75/65 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6263 FL ≤0.4105 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6263 FL ≤0.4105 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.640 |  |  |  | ≥4.640
|  |  | Medium - 120℉ LWT |  |  | ≥3.680 |  |  |  | ≥3.680
|  |  | High - 140℉ LWT |  |  | ≥2.680 |  |  |  | ≥2.680
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.550 |  |  |  | ≥3.550
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.330 |  |  |  | ≥8.330
|  |  | Medium - 120℉ LWT |  |  | ≥6.410 |  |  |  | ≥6.410
|  |  | High - 140℉ LWT |  |  | ≥4.420 |  |  |  | ≥4.420
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥6.150 |  |  |  | ≥6.150
Water source, centrifugal ≥300 & <600 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV
|  |  | 75/65 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.930 |  |  |  | ≥4.930
|  |  | Medium - 120℉ LWT |  |  | ≥3.960 |  |  |  | ≥3.960
|  |  | High - 140℉ LWT |  |  | ≥2.970 |  |  |  | ≥2.970
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.900 |  |  |  | ≥3.900
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.900 |  |  |  | ≥8.900
|  |  | Medium - 120℉ LWT |  |  | ≥6.980 |  |  |  | ≥6.980
|  |  | High - 140℉ LWT |  |  | ≥5.000 |  |  |  | ≥5.000
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥6.850 |  |  |  | ≥6.850
Water source, centrifugal ≥600 ton
|  |  | Cooling-only operation |  |  | Path A | Path B |  |  | Path A | Path B
|  |  | 54/44 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV
|  |  | 75/65 WT |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV |  |  | ≤0.5895 FL ≤0.5263 IPLV | ≤0.6158 FL ≤0.4000 IPLV
Heat-pump heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥4.930 |  |  |  | ≥4.930
|  |  | Medium - 120℉ LWT |  |  | ≥3.960 |  |  |  | ≥3.960
|  |  | High - 140℉ LWT |  |  | ≥2.970 |  |  |  | ≥2.970
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat-pump heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥3.900 |  |  |  | ≥3.900
Heat recovery chiller heating, 54/44 WT
|  |  | Low - 105℉ LWT |  |  | ≥8.900 |  |  |  | ≥8.900
|  |  | Medium - 120℉ LWT |  |  | ≥6.980 |  |  |  | ≥6.980
|  |  | High - 140℉ LWT |  |  | ≥5.000 |  |  |  | ≥5.000
|  |  | Boost - 140℉ LWT |  |  | NA |  |  |  | NA
Heat recovery chiller heating, 75/65 WT
|  |  | Low - 105℉ LWT |  |  | NA |  |  |  | NA
|  |  | Medium - 120℉ LWT |  |  | NA |  |  |  | NA
|  |  | High - 140℉ LWT |  |  | NA |  |  |  | NA
|  |  | Boost - 140℉ LWT |  |  | ≥6.850 |  |  |  | ≥6.850
Electrically Operated Room Air Conditioners
With louvered sides
|  |  | <6,000 Btu/h | 9.7 SEER | 11.0 CEER | 11.0 CEER |  | 9.7 SEER |  | 11.0 CEER
|  |  | ≥6,000 and <8,000 Btu/h | 9.7 EER | 11.0 CEER | 11.0 CEER |  | 9.7 EER |  | 11.0 CEER
|  |  | ≥8,000 and <14,000 Btu/h | 9.8 EER | 10.9 CEER | 10.9 CEER |  | 9.8 EER |  | 10.9 CEER
|  |  | ≥14,000 and <20,000 Btu/h | 9.7 EER | 10.7 CEER | 10.7 CEER |  | 9.7 EER |  | 10.7 CEER
|  |  | ≥20,000 and <28,000 Btu/h | 8.5 EER | 9.4 CEER | 9.4 CEER |  | 8.5 EER |  | 9.4 CEER
|  |  | ≥28,000 Btu/h | 8.5 EER | 9.0 CEER | 9.0 CEER |  | 8.5 EER |  | 9.0 CEER
Without louvered sides
|  |  | <6,000 Btu/h | 9.0 EER | 10.0 CEER | 10.0 CEER |  | 9.0 EER |  | 10.0 CEER
|  |  | ≥6,000 and <8,000 Btu/h | 9.0 EER | 10.0 CEER | 10.0 CEER |  | 9.0 EER |  | 10.0 CEER
|  |  | ≥8,000 and <11,000 Btu/h | 8.5 EER | 9.6 CEER | 9.6 CEER |  | 8.5 EER |  | 9.6 CEER
|  |  | ≥11,000 and <14,000 Btu/h | 8.5 EER | 9.5 CEER | 9.5 CEER |  | 8.5 EER |  | 9.5 CEER
|  |  | ≥14,000 and <20,000 Btu/h | 8.5 EER | 9.3 CEER | 9.3 CEER |  | 8.5 EER |  | 9.3 CEER
|  |  | ≥20,000 Btu/h | 8.5 EER | 9.4 CEER | 9.4 CEER |  | 8.5 EER |  | 9.4 CEER
Heat pumps with louvered sides
|  |  | <20,000 Btu/h | 9.0 EER | 9.8 CEER | 9.8 CEER |  | 9.0 EER |  | 9.8 CEER
|  |  | ≥20,000 Btu/h | 8.5 EER | 9.3 CEER | 9.3 CEER |  | 8.5 EER |  | 9.3 CEER
Heat pumps without louvered sides
|  |  | <14,000 Btu/h | 8.5 EER | 9.3 CEER | 9.3 CEER |  | 8.5 EER |  | 9.3 CEER
|  |  | ≥14,000 Btu/h | 8.0 EER | 8.7 CEER | 8.7 CEER |  | 8.0 EER |  | 8.7 CEER
|  | Casement only |  | 8.7 EER | 9.5 CEER | 9.5 CEER |  | 8.7 EER |  | 9.5 CEER
|  | Casement-slider |  | 9.5 EER | 10.4 CEER | 10.4 CEER |  | 9.5 EER |  | 10.4 CEER
Water Chiller, Air Cooled, with Condenser, Electrically Operated
|  |  | <150 tons: Path A | ≥10.100 EER FL ≥13.700 EER IPLV | ≥10.100 EER FL ≥13.700 EER IPLV | ≥10.100 EER FL ≥13.700 EER IPLV |  | ≥10.100 EER FL ≥13.700 EER IPLV |  | ≥10.100 EER FL ≥13.700 EER IPLV
|  |  | <150 tons: Path B | ≥9.700 EER FL ≥15.800 EER IPLV | ≥9.700 EER FL ≥15.800 EER IPLV | ≥9.700 EER FL ≥15.800 EER IPLV |  | ≥9.700 EER FL ≥15.800 EER IPLV |  | ≥9.700 EER FL ≥15.800 EER IPLV
|  |  | ≥150 tons: Path A | ≥10.100 EER FL ≥14.000 EER IPLV | ≥10.100 EER FL ≥14.000 EER IPLV | ≥10.100 EER FL ≥14.000 EER IPLV |  | ≥10.100 EER FL ≥14.000 EER IPLV |  | ≥10.100 EER FL ≥14.000 EER IPLV
|  |  | ≥150 tons: Path B | ≥9.7 EER FL ≥16.100 EER IPLV | ≥9.7 EER FL ≥16.100 EER IPLV | ≥9.7 EER FL ≥16.100 EER IPLV |  | ≥9.7 EER FL ≥16.100 EER IPLV |  | ≥9.7 EER FL ≥16.100 EER IPLV
Water Chiller, Air Cooled, without Condenser, Electrically Operated
|  |  | All Capacities | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements |  | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements |  | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements
Water Chiller, Water Cooled, Electrically Operated, Positive Displacement
|  |  | <75 tons: Path A | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV |  | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV |  | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV
|  |  | <75 tons: Path B | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥75 & <150 tons: Path A | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV |  | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV |  | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV
|  |  | ≥75 & <150 tons: Path B | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV |  | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV |  | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path A | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV |  | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV |  | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path B | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV |  | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV |  | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV
|  |  | ≥300 & <600 tons: Path A | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV |  | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV |  | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV
|  |  | ≥300 & <600 tons: Path B | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV |  | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV |  | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV
|  |  | ≥600 tons Path A | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥600 tons Path B | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV |  | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV |  | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV
Water Chiller, Water Cooled, Electrically Operated, Centrifugal
|  |  | <150 tons: Path A | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV |  | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV |  | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV
|  |  | <150 tons: Path B | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV |  | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV |  | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path A | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV |  | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV |  | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path B | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV |  | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV |  | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV
|  |  | ≥300 & <400 tons: Path A | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV
|  |  | ≥300 & <400 tons: Path B | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV |  | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV |  | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV
|  |  | ≥400 & <600 tons: Path A | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥400 & <600 tons: Path B | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV |  | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV |  | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV
|  |  | ≥600 tons: Path A | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV |  | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥600 tons: Path B | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV |  | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV |  | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV
Water Chiller, Air Cooled Absorption Single Effect
|  |  | All Capacities: Path A | ≥0.600 COP FL | ≥0.600 COP FL | ≥0.600 COP FL |  | ≥0.600 COP FL |  | ≥0.600 COP FL
|  |  | All Capacities: Path B | NA | NA | NA |  | NA |  | NA
Water Chiller, Water Cooled Absorption Single Effect
|  |  | All Capacities: Path A | ≥0.700 COP FL | ≥0.700 COP FL | ≥0.700 COP FL |  | ≥0.700 COP FL |  | ≥0.700 COP FL
|  |  | All Capacities: Path B | NA | NA | NA |  | NA |  | NA
Water Chiller, Absorption Double Effect, Indirect-Fired
|  |  | All Capacities: Path A | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV |  | ≥1.000 COP FL & ≥1.050 COP IPLV |  | ≥1.000 COP FL & ≥1.050 COP IPLV
|  |  | All Capacities: Path B | NA | NA | NA |  | NA |  | NA
Water Chiller, Absorption Double Effect, Direct-Fired
|  |  | All Capacities: Path A | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.000 IPLV |  | ≥1.000 COP FL & ≥1.000 IPLV |  | ≥1.000 COP FL & ≥1.000 IPLV
|  |  | All Capacities: Path B | NA | NA | NA |  | NA |  | NA
| Warm Air Furnaces and Combination Warm Air Furnaces/Air Conditioning Units |  |  |  |  | Before 1/1/2023 | After 1/1/2023 |  |  | Before 1/1/2023 | After 1/1/2023
|  |  | Gas-Fired <225,000 Btu/h | 78% AFUE or 80% Et | 80% AFUE or 80% Et | 80% Et | 81% Et | 78% AFUE or 80% Et
|  |  | (nonweatherized) | [6 empty] | 80% AFUE | 80% AFUE
|  |  | (weatherized) | [6 empty] | 81% AFUE | 81% AFUE
|  |  | Gas-Fired ≥225,000 Btu/h | 80% Et | 80% Et |  |  | 80% Et |  | 80% Et | 81% Et
|  |  | Oil-Fired <225,000 Btu/h | 78% AFUE or 80% Et | 83% AFUE or 80% Et | 80% Et | 82% Et | 78% AFUE or 80% Et
|  |  | (nonweatherized) | [6 empty] | 83% AFUE, PSB ≤11 W, Poff ≤11 W | 83% AFUE, PSB ≤11 W, Poff ≤11 W
|  |  | (weatherized) | [6 empty] | 78% AFUE | 78% AFUE
|  |  | Oil-Fired ≥225,000 Btu/h | 81% Et | 81% Et |  |  | 81% Et |  | 80% Et | 82% Et
Warm Air Duct Furnaces
|  |  | Gas-Fired | 80% Ec | 80% Ec | 80% Ec |  | 80% Ec |  | 80% Ec
Warm Air Unit Heaters
|  |  | Gas-Fired | 80% Ec | 80% Ec | 80% Ec |  | 80% Ec |  | 80% Ec
|  |  | Oil-Fired | 80% Ec | 80% Ec | 80% Ec |  | 80% Ec |  | 80% Ec
| Boilers, Gas-Fired |  |  |  |  | Minimum efficiency | as of 3/2/2022 |  |  | Minimum efficiency | as of 3/2/2022
|  | <300,000 Btu/h, Hot Water |  | 80% AFUE | 82% AFUE | 84% AFUE, PSB ≤9 W, Poff ≤9 W | 84% AFUE, PSB ≤9 W, Poff ≤9 W | 82% AFUE |  | 84% AFUE, PSB ≤9 W, Poff ≤9 W | 84% AFUE, PSB ≤9 W, Poff ≤9 W
|  | ≥300,000 & ≤2,500,000 Btu/h, Hot Water |  | 80% Et | 80% Et | 80% Et | 80% Et | 80% Et |  | 80% Et | 80% Et
|  | >2,500,000 Btu/h, Hot Water |  | 82% Ec | 82% Ec | 82% Ec | 82% Ec | 82% Ec |  | 82% Ec | 82% Ec
|  | <300,000 Btu/h, Steam |  | 75% AFUE | 84% AFUE | 82% AFUE, PSB ≤8 W, Poff ≤8 W | 82% AFUE, PSB ≤8 W, Poff ≤8 W | 80% AFUE |  | 82% AFUE, PSB ≤8 W, Poff ≤8 W | 82% AFUE, PSB ≤8 W, Poff ≤8 W
|  | ≥300,000 & ≤2,500,000 Btu/h, (Except Natural Draft) Steam |  | 79% Et | 79% Et | 79% Et | 79% Et | 79% Et |  | 79% Et | 79% Et
|  | >2,500,000 Btu/h, (Except Natural Draft) Steam |  | 79% Et | 79% Et | 79% Et | 79% Et | 79% Et |  | 79% Et | 79% Et
|  | ≥300,000 & ≤2,500,000 Btu/h, Natural Draft, Steam |  | 77% Et | 77% Et | 77% Et | 79% Et | 79% Et |  | 77% Et | 79% Et
|  | >2,500,000 Btu/h, Natural Draft, Steam |  | 77% Et | 77% Et | 77% Et | 79% Et | 79% Et |  | 77% Et | 79% Et
| Boilers, Oil-Fired |  |  |  |  | Minimum efficiency | as of 3/2/2022 |  |  | Minimum efficiency | as of 3/2/2022
|  | <300,000 Btu/h, Hot Water |  | 80% AFUE | 84% AFUE | 86% AFUE, PSB ≤11W, Poff ≤11 W | 86% AFUE, PSB ≤11 W, Poff ≤11 W | 84% AFUE |  | 86% AFUE, PSB ≤11W, Poff ≤11 W | 86% AFUE, PSB ≤11 W, Poff ≤11 W
|  | ≥300,000 & ≤2,500,000 Btu/h, Hot Water |  | 82% Et | 82% Et | 82% Et | 82% Et | 82% Et |  | 82% Et | 82% Et
|  | >2,500,000 Btu/h, Hot Water |  | 84% Ec | 84% Ec | 84% Ec | 84% Ec | 84% Ec |  | 84% Ec | 84% Ec
|  | <300,000 Btu/h, Steam |  | 80% AFUE | 82% AFUE | 85% AFUE, PSB ≤11W, Poff ≤11 W | 85% AFUE, PSB ≤11 W, Poff ≤11 W | 82% AFUE |  | 85% AFUE, PSB ≤11W, Poff ≤11 W | 85% AFUE, PSB ≤11 W, Poff ≤11 W
|  | ≥300,000 & ≤2,500,000 Btu/h, Steam |  | 81% Et | 81% Et | 81% Et | 81% Et | 81% Et |  | 81% Et | 81% Et
|  | >2,500,000 Btu/h, Steam |  | 81% Et | 81% Et | 81% Et | 81% Et | 81% Et |  | 81% Et | 81% Et
Heat Rejection Equipment
|  | Propeller or axial fan open-circuit cooling towers |  | ≥40.2 gpm/hp | ≥40.2 gpm/hp | ≥40.2 gpm/hp |  | ≥40.2 gpm/hp |  | ≥40.2 gpm/hp
|  | Centrifugal fan open-circuit cooling towers |  | ≥20.0 gpm/hp | ≥20.0 gpm/hp | ≥20.0 gpm/hp |  | ≥20.0 gpm/hp |  | ≥20.0 gpm/hp
|  | Propeller or axial fan closed-circuit cooling towers |  | ≥14.0 gpm/hp | ≥16.1gpm/hp | ≥16.1gpm/hp |  | ≥16.1gpm/hp |  | ≥16.1gpm/hp
|  | Centrifugal fan closed-circuit cooling towers |  | ≥7.0 gpm/hp | ≥7.0 gpm/hp | ≥7.0 gpm/hp |  | ≥7.0 gpm/hp |  | ≥7.0 gpm/hp
|  | Propeller or axial fan dry coolers (air-cooled fluid coolers) |  |  |  | ≥4.5 gpm/hp |  |  |  | ≥4.5 gpm/hp
|  | Propeller or axial fan evaporative condensers (R-448A test fluid) |  |  |  | ≥160,000 Btu/h-hp |  |  |  | ≥160,000 Btu/h-hp
|  | Propeller or axial fan evaporative condensers (Ammonia test fluid) |  | ≥134,000 Btu/h-hp | ≥134,000 Btu/h-hp | ≥134,000 Btu/h-hp |  | ≥134,000 Btu/h-hp |  | ≥134,000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (R-488A test fluid) |  |  |  | ≥137,000 Btu/h-hp |  |  |  | ≥137,000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (Ammonia test fluid) |  | ≥110,000 Btu/h-hp | ≥110,000 Btu/h-hp | ≥110,000 Btu/h-hp |  | ≥110,000 Btu/h-hp |  | ≥110,000 Btu/h-hp
|  | Propeller or axial fan evaporative condensers (R-507A test fluid) |  | ≥157,000 Btu/h-hp | ≥157,000 Btu/h-hp |  |  | ≥157,000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (R-507A test fluid) |  | ≥135,000 Btu/h-hp | ≥135,000 Btu/h-hp |  |  | ≥135,000 Btu/h-hp
|  | Air-cooled condensers |  | ≥176,000 Btu/h-hp | ≥176,000 Btu/h-hp | ≥176,000 Btu/h-hp |  | ≥176,000 Btu/h-hp |  | ≥176,000 Btu/h-hp
Heat Transfer Equipment
|  | Liquid-to-Liquid, plate type heat exchangers |  | NR | NR | Rated with AHRI 400 |  | NR |  | Rated with AHRI 400
Air Conditioners and Condensing Units Serving Computer Rooms Floor Mounted
|  |  |  | Downflow/Upflow Units Minimum SCOP-127 Efficiency | Downflow/Upflow Units Minimum SCOP-127 Efficiency |  |  | Minimum Net Sensible COP |  | Minimum Net Sensible COP
Air cooled
|  |  | <65,000 Btu/h | 2.20 / 2.09 | 2.20 / 2.09
|  |  | ≥65,000 & <240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥240,000 Btu/h | 1.90 / 1.79 | 1.90 / 1.79
Air cooled
|  |  | 85°F/52°F (Class 2) |  |  | Downflow | Upflow - ducted |  |  | Downflow | Upflow - ducted
|  |  | <80,000 Btu/h |  |  | 2.7 | 2.67 |  |  | 2.7 | 2.67
|  |  | ≥80,000 & <295,000 Btu/h |  |  | 2.58 | 2.55 |  |  | 2.58 | 2.55
|  |  | ≥295,000 Btu/h |  |  | 2.36 | 2.33 |  |  | 2.36 | 2.33
|  |  | 85°F/52°F (Class 1) |  |  | Upflow - nonducted |  |  |  | Upflow - nonducted
|  |  | <65,000 Btu/h |  |  | 2.16 |  |  |  | 2.16
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.04 |  |  |  | 2.04
|  |  | ≥240,000 Btu/h |  |  | 1.89 |  |  |  | 1.89
|  |  | 95°F/52°F (Class 3) |  |  | Horizontal |  |  |  | Horizontal
|  |  | <65,000 Btu/h |  |  | 2.65 |  |  |  | 2.65
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.55 |  |  |  | 2.55
|  |  | ≥240,000 Btu/h |  |  | 2.47 |  |  |  | 2.47
Air cooled with fluid economizer
|  |  | 85°F/52°F (Class 1) |  |  | Downflow | Upflow - ducted |  |  | Downflow | Upflow - ducted
|  |  | <80,000 Btu/h |  |  | 2.7 | 2.67 |  |  | 2.7 | 2.67
|  |  | ≥80,000 & <295,000 Btu/h |  |  | 2.58 | 2.55 |  |  | 2.58 | 2.55
|  |  | ≥295,000 Btu/h |  |  | 2.36 | 2.33 |  |  | 2.36 | 2.33
|  |  | 75°F/52°F (Class 1) |  |  | Upflow - nonducted |  |  |  | Upflow - nonducted
|  |  | <65,000 Btu/h |  |  | 2.09 |  |  |  | 2.09
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 1.99 |  |  |  | 1.99
|  |  | ≥240,000 Btu/h |  |  | 1.81 |  |  |  | 1.81
|  |  | 95°F/52°F (Class 3) |  |  | Horizontal |  |  |  | Horizontal
|  |  | <65,000 Btu/h |  |  | 2.65 |  |  |  | 2.65
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.55 |  |  |  | 2.55
|  |  | ≥240,000 Btu/h |  |  | 2.47 |  |  |  | 2.47
Air cooled
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2.09
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.45
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.2
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.05
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 1.99
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.35
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 1.85
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 1.79
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.15
Water cooled
|  |  | <65,000 Btu/h | 2.60 / 2.49 | 2.60 / 2.49
|  |  | ≥65,000 & <240,000 Btu/h | 2.50 / 2.39 | 2.50 / 2.39
|  |  | ≥240,000 Btu/h | 2.40 / 2.29 | 2.40 / 2.29
Water cooled
|  |  | 85°F/52°F (Class 1) |  |  | Downflow | Upflow - ducted |  |  | Downflow | Upflow - ducted
|  |  | <80,000 Btu/h |  |  | 2.82 | 2.79 |  |  | 2.82 | 2.79
|  |  | ≥80,000 & <295,000 Btu/h |  |  | 2.73 | 2.7 |  |  | 2.73 | 2.7
|  |  | ≥295,000 Btu/h |  |  | 2.67 | 2.64 |  |  | 2.67 | 2.64
|  |  | 75°F/52°F (Class 1) |  |  | Upflow - nonducted |  |  |  | Upflow - nonducted
|  |  | <65,000 Btu/h |  |  | 2.43 |  |  |  | 2.43
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.32 |  |  |  | 2.32
|  |  | ≥240,000 Btu/h |  |  | 2.2 |  |  |  | 2.2
|  |  | 95°F/52°F (Class 3) |  |  | Horizontal |  |  |  | Horizontal
|  |  | <65,000 Btu/h |  |  | 2.79 |  |  |  | 2.79
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.68 |  |  |  | 2.68
|  |  | ≥240,000 Btu/h |  |  | 2.6 |  |  |  | 2.6
Water cooled with fluid economizer
|  |  | 85°F/52°F (Class 1) |  |  | Downflow | Upflow - ducted |  |  | Downflow | Upflow - ducted
|  |  | <80,000 Btu/h |  |  | 2.77 | 2.74 |  |  | 2.77 | 2.74
|  |  | ≥80,000 & <295,000 Btu/h |  |  | 2.68 | 2.65 |  |  | 2.68 | 2.65
|  |  | ≥295,000 Btu/h |  |  | 2.61 | 2.58 |  |  | 2.61 | 2.58
|  |  | 75°F/52°F (Class 1) |  |  | Upflow - nonducted |  |  |  | Upflow - nonducted
|  |  | <65,000 Btu/h |  |  | 2.35 |  |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.24 |  |  |  | 2.24
|  |  | ≥240,000 Btu/h |  |  | 2.12 |  |  |  | 2.12
|  |  | 95°F/52°F (Class 3) |  |  | Horizontal |  |  |  | Horizontal
|  |  | <65,000 Btu/h |  |  | 2.71 |  |  |  | 2.71
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.6 |  |  |  | 2.6
|  |  | ≥240,000 Btu/h |  |  | 2.54 |  |  |  | 2.54
Water cooled
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.5
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2.25
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.7
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.4
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.2
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2.15
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.6
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.25
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.1
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2.05
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.45
Water cooled with fluid economizer
|  |  | <65,000 Btu/h | 2.55 / 2.44 | 2.55 / 2.44
|  |  | ≥65,000 & <240,000 Btu/h | 2.45 / 2.34 | 2.45 / 2.34
|  |  | ≥240,000 Btu/h | 2.35 / 2.24 | 2.35 / 2.24
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.45
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.25
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2.2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.6
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.15
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2.1
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.55
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.2
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.05
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.4
Glycol cooled
|  |  | <65,000 Btu/h | 2.50 / 2.39 | 2.50 / 2.39
|  |  | ≥65,000 & <240,000 Btu/h | 2.15 / 2.04 | 2.15 / 2.04
|  |  | ≥240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
Glycol cooled
|  |  | 85°F/52°F (Class 1) |  |  | Downflow | Upflow - ducted |  |  | Downflow | Upflow - ducted
|  |  | <80,000 Btu/h |  |  | 2.56 | 2.53 |  |  | 2.56 | 2.53
|  |  | ≥80,000 & <295,000 Btu/h |  |  | 2.24 | 2.21 |  |  | 2.24 | 2.21
|  |  | ≥295,000 Btu/h |  |  | 2.21 | 2.18 |  |  | 2.21 | 2.18
|  |  | 75°F/52°F (Class 1) |  |  | Upflow - nonducted |  |  |  | Upflow - nonducted
|  |  | <65,000 Btu/h |  |  | 2.08 |  |  |  | 2.08
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 1.9 |  |  |  | 1.9
|  |  | ≥240,000 Btu/h |  |  | 1.81 |  |  |  | 1.81
|  |  | 95°F/52°F (Class 3) |  |  | Horizontal |  |  |  | Horizontal
|  |  | <65,000 Btu/h |  |  | 2.48 |  |  |  | 2.48
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.18 |  |  |  | 2.18
|  |  | ≥240,000 Btu/h |  |  | 2.18 |  |  |  | 2.18
Glycol cooled with fluid economizer
|  |  | 85°F/52°F (Class 1) |  |  | Downflow | Upflow - ducted |  |  | Downflow | Upflow - ducted
|  |  | <80,000 Btu/h |  |  | 2.51 | 2.48 |  |  | 2.51 | 2.48
|  |  | ≥80,000 & <295,000 Btu/h |  |  | 2.19 | 2.16 |  |  | 2.19 | 2.16
|  |  | ≥295,000 Btu/h |  |  | 2.15 | 2.12 |  |  | 2.15 | 2.12
|  |  | 75°F/52°F (Class 1) |  |  | Upflow - nonducted |  |  |  | Upflow - nonducted
|  |  | <65,000 Btu/h |  |  | 2 |  |  |  | 2
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 1.82 |  |  |  | 1.82
|  |  | ≥240,000 Btu/h |  |  | 1.73 |  |  |  | 1.73
|  |  | 95°F/52°F (Class 3) |  |  | Horizontal |  |  |  | Horizontal
|  |  | <65,000 Btu/h |  |  | 2.44 |  |  |  | 2.44
|  |  | ≥65,000 & <240,000 Btu/h |  |  | 2.1 |  |  |  | 2.1
|  |  | ≥240,000 Btu/h |  |  | 2.1 |  |  |  | 2.1
Glycol cooled
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.4
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.05
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 1.85
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 1.85
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.15
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 1.95
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 1.8
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 1.75
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.1
Glycol cooled with fluid economizer
|  |  | <65,000 Btu/h | 2.45 / 2.34 | 2.45 / 2.34
|  |  | ≥65,000 & <240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥240,000 Btu/h | 2.05 / 1.94 | 2.05 / 1.94
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 2.25
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 1.95
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 1.8
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 1.75
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.1
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  |  |  | 1.9
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  |  |  | 1.8
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  |  |  | 1.7
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  |  |  | 2.1
Air Conditioners and Condensing Units Serving Computer Rooms Ceiling Mounted
|  | Air cooled with free air discharge condenser | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 2.05 | 2.08
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 2.02 | 2.05
|  |  | ≥65,000 Btu/h | [6 empty] | 1.92 | 1.94
|  | Air cooled with free air discharge condenser with fluid economizer | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 2.01 | 2.04
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 1.97 | 2
|  |  | ≥65,000 Btu/h | [6 empty] | 1.87 | 1.89
|  | Air cooled with ducted condenser | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 1.86 | 1.89
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 1.83 | 1.86
|  |  | ≥65,000 Btu/h | [6 empty] | 1.73 | 1.75
|  | Air cooled with fluid economizer and ducted condenser | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 1.82 | 1.85
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 1.78 | 1.81
|  |  | ≥65,000 Btu/h | [6 empty] | 1.68 | 1.7
|  | Water cooled | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 2.38 | 2.41
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 2.28 | 2.31
|  |  | ≥65,000 Btu/h | [6 empty] | 2.18 | 2.2
|  | Water cooled with fluid economizer | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 2.33 | 2.36
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 2.23 | 2.26
|  |  | ≥65,000 Btu/h | [6 empty] | 2.13 | 2.16
|  | Glycol cooled | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 1.97 | 2
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 1.93 | 1.98
|  |  | ≥65,000 Btu/h | [6 empty] | 1.78 | 1.81
|  | Glycol cooled with fluid economizer | [7 empty] | Ducted | Nonducted
|  |  | <29,000 Btu/h | [6 empty] | 1.92 | 1.95
|  |  | ≥29,000 & <65,000 Btu/h | [6 empty] | 1.88 | 1.93
|  |  | ≥65,000 Btu/h | [6 empty] | 1.73 | 1.76
Variable Refrigerant Flow (VRF) Systems
VFR Multi-Split Air Conditioners, Air Cooled
|  |  | <65,000 Btu/h, All heating section |  |  | 13.0 SEER |  | 13.0 SEER |  | 13.0 SEER
|  |  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section |  |  | 11.2 EER 13.1 IEER 15.5 IEER |  | 11.2 EER 15.5 IEER |  | 11.2 EER 13.1 IEER 15.5 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section |  |  | 11.0 EER 12.9 IEER 14.9 IEER |  | 11.0 EER 14.9 IEER |  | 11.0 EER 12.9 IEER 14.9 IEER
|  |  | ≥240,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.0 EER 11.6 IEER 13.9 IEER |  | 10.0 EER 13.9 IEER |  | 10.0 EER 11.6 IEER 13.9 IEER
VFR Multi-Split Heat Pumps, Air Cooled (Cooling Mode)
|  |  | <65,000 Btu/h, All heating section |  |  | 13.0 SEER |  | 13.0 SEER |  | 13.0 SEER
|  |  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section |  |  | 11.0 EER 12.9 IEER 14.6 IEER |  | 11.0 EER 14.6 IEER |  | 11.0 EER 12.9 IEER 14.6 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.6 EER 12.3 IEER 13.9 IEER |  | 10.6 EER 13.9 IEER |  | 10.6 EER 12.3 IEER 13.9 IEER
|  |  | ≥240,000 Btu/h, Electric resistance (or none) heating section |  |  | 9.5 EER 11.0 IEER 12.7 IEER |  | 9.5 EER 12.7 IEER |  | 9.5 EER 11.0 IEER 12.7 IEER
VFR Multi-Split with Heat Recovery Heat Pumps, Air Cooled (Cooling Mode)
|  |  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.8 EER 12.7 IEER 14.4 IEER |  | 10.8 EER 14.4 IEER |  | 10.8 EER 12.7 IEER 14.4 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.4 EER 12.1 IEER 13.7 IEER |  | 10.4 EER 13.7 IEER |  | 10.4 EER 12.1 IEER 13.7 IEER
|  |  | ≥240,000 Btu/h, Electric resistance (or none) heating section |  |  | 9.3 EER 10.8 IEER 12.5 IEER |  | 9.3 EER 12.5 IEER |  | 9.3 EER 10.8 IEER 12.5 IEER
VFR Multi-Split Heat Pumps, Water Source (Cooling Mode) 86º Entering Water
|  |  | <65,000 Btu/h, All heating section |  |  | 12.0 EER 16.0 IEER |  | 12.0 EER 16.0 IEER |  | 12.0 EER 16.0 IEER
|  |  | ≥65,000 & <135,000 Btu/h, All heating section |  |  | 12.0 EER 16.0 IEER |  | 12.0 EER 16.0 IEER |  | 12.0 EER 16.0 IEER
|  |  | ≥135,000 & <240,000 Btu/h, All Heating Section |  |  | 10.0 EER 14.0 IEER |  | 10.0 EER 14.0 IEER |  | 10.0 EER 14.0 IEER
|  |  | ≥240,000 Btu/h, All Heating Section |  |  | 10.0 EER 12.0 IEER |  | 10.0 EER 12.0 IEER |  | 10.0 EER 12.0 IEER
VFR Multi-Split Heat Pumps with Heat Recovery, Water Source (Cooling Mode) 86º Entering Water
|  |  | <65,000 Btu/h, All heating section |  |  | 11.8 EER 15.8 IEER |  | 11.8 EER 15.8 IEER |  | 11.8 EER 15.8 IEER
|  |  | ≥65,000 & <135,000 Btu/h, All heating section |  |  | 11.8 EER 15.8 IEER |  | 11.8 EER 15.8 IEER |  | 11.8 EER 15.8 IEER
|  |  | ≥135,000 & <240,000 Btu/h, All Heating Section |  |  | 9.8 EER 13.8 IEER |  | 9.8 EER 13.8 IEER |  | 9.8 EER 13.8 IEER
|  |  | ≥240,000 Btu/h, All Heating Section |  |  | 9.8 EER 11.8 IEER |  | 9.8 EER 11.8 IEER |  | 9.8 EER 11.8 IEER
VFR Multi-Split Heat Pumps, Groundwater Source (Cooling Mode) 59º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 16.2 EER |  | 16.2 EER |  | 16.2 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 13.8 EER |  | 13.8 EER |  | 13.8 EER
VFR Multi-Split Heat Pumps with Heat Recovery, Groundwater Source (Cooling Mode) 59º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 16.0 EER |  | 16.0 EER |  | 16.0 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 13.6 EER |  | 13.6 EER |  | 13.6 EER
VFR Multi-Split Heat Pumps, Ground Source (Cooling Mode) 77º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 13.4 EER |  | 13.4 EER |  | 13.4 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 11.0 EER |  | 11.0 EER |  | 11.0 EER
VFR Multi-Split Heat Pumps with Heat Recovery, Ground Source (Cooling Mode) 77º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 13.2 EER |  | 13.2 EER |  | 13.2 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 10.8 EER |  | 10.8 EER |  | 10.8 EER
VFR Multi-Split Heat Pumps, Air Cooled (Heating Mode)
|  |  | <65,000 Btu/h (cooling capacity) |  |  | 7.7 HSPF |  | 7.7 HSPF |  | 7.7 HSPF
≥65,000 & <135,000 Btu/h (cooling capacity)
|  |  | 47ºF db / 43ºF wb |  |  | 3.3 COPH |  | 3.3 COPH |  | 3.3 COPH
|  |  | 17ºF db / 15ºF wb |  |  | 2.25 COPH |  | 2.25 COPH |  | 2.25 COPH
≥135,000 (cooling capacity)
|  |  | 47ºF db / 43ºF wb |  |  | 3.2 COPH |  | 3.2 COPH |  | 3.2 COPH
|  |  | 17ºF db / 15ºF wb |  |  | 2.05 COPH |  | 2.05 COPH |  | 2.05 COPH
VFR Multi-Split Heat Pumps, Water Source (Heating Mode) 68º Entering Water
|  |  | <65,000 Btu/h (Cooling Capacity) |  |  | 4.2 COPH 4.3 COPH |  | 4.3 COPH |  | 4.2 COPH 4.3 COPH
|  |  | ≥65,000 & <135,000 Btu/h (Cooling Capacity) |  |  | 4.2 COPH 4.3 COPH |  | 4.3 COPH |  | 4.2 COPH 4.3 COPH
|  |  | ≥135,000 & <240,000 Btu/h (Cooling Capacity) |  |  | 3.9 COPH 4.0 COPH |  | 4.0 COPH |  | 3.9 COPH 4.0 COPH
|  |  | ≥240,000 Btu/h (Cooling Capacity) |  |  | 3.9 COPH |  | 3.9 COPH |  | 3.9 COPH
VFR Multi-Split Heat Pumps, Groundwater Source (Heating Mode) 50º Entering Water
|  |  | <135,000 Btu/h (cooling capacity) |  |  | 3.6 COPH |  | 3.6 COPH |  | 3.6 COPH
|  |  | ≥135,000 Btu/h (cooling capacity) |  |  | 3.3 COPH |  | 3.3 COPH |  | 3.3 COPH
VFR Multi-Split Heat Pumps, Ground Source (Heating Mode) 32º Entering Water
|  |  | <135,000 Btu/h (cooling capacity) |  |  | 3.1 COPH |  | 3.1 COPH |  | 3.1 COPH
|  |  | ≥135,000 Btu/h (cooling capacity) |  |  | 2.8 COPH |  | 2.8 COPH |  | 2.8 COPH
Vapor Compression Based Indoor Pool Dehumidifiers
|  | Single package indoor without air-cooled condenser (with or without economizer) |  |  |  | 3.5 MRE |  | 3.5 MRE |  | 3.5 MRE
|  | Single package water-cooled (with or without economizer) |  |  |  | 3.5 MRE |  | 3.5 MRE |  | 3.5 MRE
|  | Single package air-cooled (with or without economizer) |  |  |  | 3.5 MRE |  | 3.5 MRE |  | 3.5 MRE
|  | Split system air-cooled (with or without economizer) |  |  |  | 3.5 MRE |  | 3.5 MRE |  | 3.5 MRE
Dedicated Outdoor Air Units
Direct Expansion, Electrically Operated, Single-Package and Remote Condenser, without Energy Recovery
|  |  | Air cooled (dehumidification mode) |  |  | 4.0 ISMRE |  | 4.0 ISMRE |  | 4.0 ISMRE
|  |  | Air source heat pump (dehumidification mode) |  |  | 4.0 ISMRE |  | 4.0 ISMRE |  | 4.0 ISMRE
|  |  | Water cooled with cooling tower condenser water (dehumidification mode) |  |  | 4.9 ISMRE |  | 4.9 ISMRE |  | 4.9 ISMRE
|  |  | Water cooled with chilled water (dehumidification mode) |  |  | 6.0 ISMRE |  | 6.0 ISMRE |  | 6.0 ISMRE
|  |  | Air source heat pump (heating mode) |  |  | 2.7 ISCOP |  | 2.7 ISCOP |  | 2.7 ISCOP
|  |  | Closed loop ground source heat pump (dehumidification mode) |  |  | 4.8 ISMRE |  | 4.8 ISMRE |  | 4.8 ISMRE
|  |  | Ground-water source heat pump (dehumidification mode) |  |  | 5.0 ISMRE |  | 5.0 ISMRE |  | 5.0 ISMRE
|  |  | Water source heat pump (dehumidification mode) |  |  | 4.0 ISMRE |  | 4.0 ISMRE |  | 4.0 ISMRE
|  |  | Closed loop ground source heat pump (heating mode) |  |  | 2.0 ISCOP |  | 2.0 ISCOP |  | 2.0 ISCOP
|  |  | Ground-water source heat pump (heating mode) |  |  | 3.2 ISCOP |  | 3.2 ISCOP |  | 3.2 ISCOP
|  |  | Water source heat pump (heating mode) |  |  | 3.5 ISCOP |  | 3.5 ISCOP |  | 3.5 ISCOP
Direct Expansion, Electrically Operated, Single-Package and Remote Condenser, with Energy Recovery
|  |  | Air cooled (dehumidification mode) |  |  | 5.2 ISMRE |  | 5.2 ISMRE |  | 5.2 ISMRE
|  |  | Air source heat pump (dehumidification mode) |  |  | 5.2 ISMRE |  | 5.2 ISMRE |  | 5.2 ISMRE
|  |  | Water cooled with cooling tower condenser water (dehumidification mode) |  |  | 5.3 ISMRE |  | 5.3 ISMRE |  | 5.3 ISMRE
|  |  | Water cooled with chilled water (dehumidification mode) |  |  | 6.6 ISMRE |  | 6.6 ISMRE |  | 6.6 ISMRE
|  |  | Air source heat pump (heating mode) |  |  | 3.3 ISCOP |  | 3.3 ISCOP |  | 3.3 ISCOP
|  |  | Closed loop ground source heat pump (dehumidification mode) |  |  | 5.2 ISMRE |  | 5.2 ISMRE |  | 5.2 ISMRE
|  |  | Ground-water source heat pump (dehumidification mode) |  |  | 5.8 ISMRE |  | 5.8 ISMRE |  | 5.8 ISMRE
|  |  | Water source heat pump (dehumidification mode) |  |  | 4.8 ISMRE |  | 4.8 ISMRE |  | 4.8 ISMRE
|  |  | Closed loop ground source heat pump (heating mode) |  |  | 3.8 ISCOP |  | 3.8 ISCOP |  | 3.8 ISCOP
|  |  | Ground-water source heat pump (heating mode) |  |  | 4.0 ISCOP |  | 4.0 ISCOP |  | 4.0 ISCOP
|  |  | Water source heat pump (heating mode) |  |  | 4.8 ISCOP |  | 4.8 ISCOP |  | 4.8 ISCOP
HVAC Controls
Zone Thermostatic Controls
|  |  | Location | Within each zone | Within each zone | Within each zone |  | Within each zone |  | Within each zone
|  |  | Dwelling unit |  |  |  |  | Single zone |  | Single zone
|  |  | Humidity control systems | At least one control per system where required | At least one control per system where provided | At least one control per system where provided |  | Prevent simultaneous operation of humidification & dehumidification equipment |  | Prevent simultaneous operation of humidification & dehumidification equipment
[8 empty] | Prevent use of fossil fuel or electricity to produce >30% relative humidity in warmest zone or <60% relative humidity in coldest zone |  | Prevent use of fossil fuel or electricity to produce >30% relative humidity in warmest zone or <60% relative humidity in coldest zone
|  |  | Perimeter system | Per each exterior exposure per orientation | Per each exterior exposure per orientation | Per each exterior exposure per orientation |  | Per each exterior exposure per orientation |  | Per each exterior exposure per orientation
|  |  | Dead band between heating & cooling | ≥5º | ≥5º | ≥5º |  | ≥5º |  | ≥5º
|  |  | Heating system supply water temperature reset based on outdoor temperature | Required | Required | Required |  | Required on systems >300,000 Btu/h design capacity |  | Required on systems >300,000 Btu/h design capacity
|  |  | Set point overlap restriction where separate heating & cooling controls located in zone | Required | Required | Required |  | Required |  | Required
Off-Hour Controls
|  |  | Automatic setback and shutdown | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor |  | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor |  | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor
|  |  | Setback capabilities | Down to 55° or Up to 85° | Down to 55° or Up to 85° | Down to 55° or Up to 85° |  | Adjustable heating ≥10° below occupied heating setpoint |  | Adjustable heating ≥10° below occupied heating setpoint
[8 empty] | Adjustable cooling ≥5° above occupied cooling setpoint or to prevent high space humidity levels |  | Adjustable cooling ≥5° above occupied cooling setpoint or to prevent high space humidity levels
|  |  | Optimum start controls | Automatic start to achieve desired temperature just prior to scheduled occupancy | Automatic start to achieve desired temperature just prior to scheduled occupancy | Automatic start to achieve desired temperature just prior to scheduled occupancy. Automatic stop on each system with DDC of individual zones |  | On individual heating and cooling systems with setback controls and DDC |  | On individual heating and cooling systems with setback controls and DDC
|  |  | Zone isolation | Required for nonsimultaneously occupied zones | Required for nonsimultaneously occupied zones | Required for nonsimultaneously occupied zones |  | Required for nonsimultaneously occupied zones |  | Required for nonsimultaneously occupied zones
|  |  |  | Isolation zones <25,000 sf or 1 floor | Isolation zones <25,000 sf or 1 floor | Isolation zones <25,000 sf or 1 floor |  | Isolation zones <25,000 sf or 1 floor |  | Isolation zones <25,000 sf or 1 floor
|  |  |  | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area |  | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area |  | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area
|  |  | Exceptions to off-hour controls | Zone that operate continuously | Zone that operate continuously | Zone that operate continuously |  | Continuous Operation |  | Continuous Operation
|  |  |  | Zone full HVAC load <6,800 Btu/h with readily accessible manual on/off | Zone full HVAC load <6,800 Btu/h with readily accessible manual on/off | Zone full HVAC load <6,800 Btu/h with readily accessible manual on/off |  | Systems <15,000 Btu/h with readily accessible manual on/off |  | Systems <15,000 Btu/h with readily accessible manual on/off
|  |  | Automatic HVAC Controls in Hotel/Motel Guest Rooms |  | In hotels & motels with >50 guest rooms | In hotels & motels with >50 guest rooms |  | In hotels & motels with >50 guest rooms |  | In hotels & motels with >50 guest rooms
[5 empty] | Automatically raise occupant set point ≥4° in cooling mode within 30 minutes of occupants leaving guest room | When rented & unoccupied: Automatically raise occupant set point ≥4° in cooling mode within 30 minutes of occupants leaving guest room |  | Automatically raise occupant set point ≥4° in cooling mode within 30 minutes of occupants leaving guest room |  | When rented & unoccupied: Automatically raise occupant set point ≥4° in cooling mode within 20 minutes of occupants leaving guest room
[5 empty] | Automatically lower occupant set point ≥4° in heating mode within 30 minutes of occupants leaving guest room | When rented & unoccupied: Automatically lower occupant set point ≥4° in heating mode within 30 minutes of occupants leaving guest room |  | Automatically lower occupant set point ≥4° in heating mode within 30 minutes of occupants leaving guest room |  | When rented & unoccupied: Automatically lower occupant set point ≥4° in heating mode within 20 minutes of occupants leaving guest room
[5 empty] | When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode | When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode |  | When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode |  | When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode
[5 empty] | Within 30 of occupants leaving room, automatically turn off ventilation and exhaust fans or | Within 20 of occupants leaving room, automatically turn off ventilation and exhaust fans or |  | Within 30 of occupants leaving room, automatically turn off ventilation and exhaust fans or |  | Within 20 of occupants leaving room, automatically turn off ventilation and exhaust fans or
[5 empty] | Automatically shut off supply of outdoor air & shut off exhaust air | Automatically shut off supply of outdoor air & shut off exhaust air |  | Automatically shut off supply of outdoor air & shut off exhaust air |  | Automatically shut off supply of outdoor air & shut off exhaust air
[5 empty] | Captive key card systems permitted to be used to comply | Captive key card systems permitted to be used to indicate occupancy |  | Captive key card systems permitted to be used to comply |  | Captive key card systems permitted to be used to indicate occupancy
|  |  | Ventilation fans |  |  |  |  | Automatic shutoff fans >0.75 hp when not required |  | Automatic shutoff fans >0.75 hp when not required
Shutoff Dampers
|  |  | Stair and shaft vents, buildings ≥3 Stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Stair and shaft vents, buildings <3 stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Outdoor air supply (intake) & exhaust, buildings ≥3 stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate or nonmotorized dampers for capacities ≤300 cfm
|  |  | Outdoor air supply, buildings <3 stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate |  | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Nonmotorized dampers | Gravity dampers with maximum leakage rate | maximum leakage rate | maximum leakage rate |  | maximum leakage rate |  | maximum leakage rate
|  |  |  | 20 cfm/sf for dampers ≥24" in either dimension or | 20 cfm/sf for dampers ≥24" in either dimension or | 20 cfm/sf for dampers ≥24" in either dimension or |  | 20 cfm/sf for dampers ≥24" in either dimension or |  | 20 cfm/sf for dampers ≥24" in either dimension or
|  |  |  | 40 cfm/sf for dampers <24" in either direction | 40 cfm/sf for dampers <24" in either direction | 40 cfm/sf for dampers <24" in either direction |  | 40 cfm/sf for dampers <24" in either direction |  | 40 cfm/sf for dampers <24" in either direction
|  |  | Automatic shutoff damper controls | Required for motorized dampers | Required for motorized dampers | Required for motorized dampers |  | Required for motorized dampers |  | Required for motorized dampers
Heat Pump Auxiliary Heat Control
|  |  | Prevent internal electric resistance heater operation when heating load can be met by heat pump alone | Required | Required | Required |  | Required |  | Required
Insulation Protection
|  |  | Protection from sunlight, moisture, equipment maintenance, wind & solar radiation | Required | Required | Required |  | Required |  | Required
|  |  | Adhesive tape | Not permitted | Not permitted | Not permitted |  | Not permitted |  | Not permitted
Freeze Protection and Snow/Ice Melting Systems
|  |  | Automatic shutoff for freeze protection systems | >40º outside air temperature or when conditions of protected fluid will prevent freezing | >40º outside air temperature or when conditions of protected fluid will prevent freezing | >40º outside air temperature or when conditions of protected fluid will prevent freezing |  | >40º outside air temperature or when conditions of protected fluid will prevent freezing |  | >40º outside air temperature or when conditions of protected fluid will prevent freezing
|  |  | Automatic shutoff for melting systems | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature |  | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature |  | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature
Ventilation
|  |  |  | Capability to reduce to minimum required | Capability to reduce to minimum required | Capability to reduce to minimum required
|  |  | Demand control ventilation to automatically reduce outside air intake during partial occupancy | Required for spaces >500 sf & average occupancy 25 persons per 1,000 sf & served by defined HVAC system | Required for spaces >500 sf & average occupancy ≥25 persons per 1,000 sf & served by defined HVAC system | Required for spaces >500 sf & average occupancy ≥15 persons per 1,000 sf & served by defined HVAC system |  | Required for spaces >500 sf & design occupancy ≥25 persons per 1,000 sf & served by defined HVAC system |  | Required for spaces >500 sf & design occupancy ≥25 persons per 1,000 sf & served by defined HVAC system
|  |  | Enclosed parking garages | ≥22,500 cfm total exhaust capacity or <1,125 cfm/hp: not utilizing heating or mechanical cooling | ≥22,500 cfm total exhaust capacity or <1,125 cfm/hp: not utilizing heating or mechanical cooling | ≥8,000 cfm total exhaust capacity or <1,125 cfm/hp: not utilizing heating or mechanical cooling |  | ≥30,000 sq. ft. or <1,500 sq. ft/ hp: not utilizing heating or mechanical cooling |  | ≥30,000 sq. ft. or <1,500 sq. ft/ hp: not utilizing heating or mechanical cooling
|  |  |  | Automatic air flow rate control to ≤50% based on contaminant levels or intermittently operate fans <20% of occupied time | Automatic air flow rate control to ≤50% based on contaminant levels or intermittently operate fans <20% of occupied time | Automatic air flow rate control to ≤50% based on contaminant levels or intermittently operate fans <20% of occupied time |  | Automatic air flow rate control to ≤50% based on contaminant levels |  | Automatic air flow rate control to ≤50% based on contaminant levels
|  |  | Ventilation air heating control |  | For units serving multiple zones & operate in conjunction with zone heating & cooling systems | For units serving multiple zones & operate in conjunction with zone heating & cooling systems |  | For units serving multiple zones & operate in conjunction with zone heating & cooling systems |  | For units serving multiple zones & operate in conjunction with zone heating & cooling systems
[5 empty] | Not use heating or heat recovery to warm supply air >60℉ when | Not use heating or heat recovery to warm supply air >60℉ when |  | Not use heating or heat recovery to warm supply air >60℉ when |  | Not use heating or heat recovery to warm supply air >60℉ when
[5 empty] | building loads or outdoor air temperature indicate majority of zones require cooling | Building loads or outdoor air temperature indicate majority of zones require cooling |  | Building loads or outdoor air temperature indicate majority of zones require cooling |  | Building loads or outdoor air temperature indicate majority of zones require cooling
Heated or Cooled Vestibules
|  |  | Controls |  | Shut off heating when outdoor air temperature >45℉ | Shut off heating when outdoor air temperature >45℉ |  | Shut off heating when outdoor air temperature >45℉ |  | Shut off heating when outdoor air temperature >45℉
[5 empty] | Thermostat located in vestibule | Thermostat located in vestibule |  | Thermostat located in vestibule |  | Thermostat located in vestibule
[5 empty] | Heating setpoint limit ≤60℉ | Heating setpoint limit ≤60℉ |  | Heating setpoint limit ≤60℉ |  | Heating setpoint limit ≤60℉
[5 empty] | Cooling setpoint limit ≥85℉ | Cooling setpoint limit ≥85℉ |  | Cooling setpoint limit ≥85℉ |  | Cooling setpoint limit ≥85℉
Direct Digital Control (DDC) Required Applications
New Buildings
|  |  | Air-handling system and all zones served by system |  |  |  |  | Individual system serving >3 zones & with fan system bhp ≥10 hp |  | Individual system serving >3 zones & with fan system bhp ≥10 hp
|  |  | Chilled-water plant and all coils and terminal units served by system |  |  |  |  | Individual plants supplying >3 zones with design cooling capacity ≥300,000 Btu/h |  | Individual plants supplying >3 zones with design cooling capacity ≥300,000 Btu/h
|  |  | Hot-water plant and all coils and terminal units served by system |  |  |  |  | Individual plants supplying >3 zones with design heating capacity ≥300,000 Btu/h |  | Individual plants supplying >3 zones with design heating capacity ≥300,000 Btu/h
Alteration or Addition
|  |  | Zone terminal unit (such as VAV box) |  |  |  |  | Where existing zones served by same air handling, chilled-water, or hot-water system have DDC |  | Where existing zones served by same air handling, chilled-water, or hot-water system have DDC
|  |  | Air-handling system or fan coil |  |  |  |  | Where existing air-handling system(s) and fan coil(s) served by same chilled-water or hot-water plant have DDC |  | Where existing air-handling system(s) and fan coil(s) served by same chilled-water or hot-water plant have DDC
|  |  | New air-handling system and all new zones served by the system |  |  |  |  | Individual systems with fan system bhp ≥10 hp and supplying >3 zones and >75% zones are new |  | Individual systems with fan system bhp ≥10 hp and supplying >3 zones and >75% zones are new
|  |  | New or upgraded chilled-water plant |  |  |  |  | Where all chillers are new and plant design cooling capacity ≥300,000 Btu/h |  | Where all chillers are new and plant design cooling capacity ≥300,000 Btu/h
|  |  | New or upgraded hot-water plant |  |  |  |  | Where all boilers are new and plan design heating capacity ≥300,000 Btu/h |  | Where all boilers are new and plan design heating capacity ≥300,000 Btu/h
Direct Digital Control (DDC) Requirements
|  |  | Control capabilities |  |  |  |  | Monitoring zone & system demand for fan pressure, pump pressure, heating and cooling |  | Monitoring zone & system demand for fan pressure, pump pressure, heating and cooling
[8 empty] | Transferring zone & system demand information from zones to air distribution system controllers and from air distribution systems to heating and cooling plant controllers |  | Transferring zone & system demand information from zones to air distribution system controllers and from air distribution systems to heating and cooling plant controllers
[8 empty] | Automatically detecting those zones and systems that may be excessively driving reset logic and generate alarm or other indication to system operator |  | Automatically detecting those zones and systems that may be excessively driving reset logic and generate alarm or other indication to system operator
[8 empty] | Readily allowing operator removal of zone(s) from reset algorithm |  | Readily allowing operator removal of zone(s) from reset algorithm
|  |  | DDC Display |  |  |  |  | Where required for new buildings, capable of trending and graphically displaying input and output points |  | Where required for new buildings, capable of trending and graphically displaying input and output points
|  |  | Chilled-water plant monitoring |  |  |  |  | Electric driven water-cooled plants >1,500 tons peak capacity |  | Electric driven water-cooled plants >1,500 tons peak capacity
[8 empty] | Electric driven air-cooled plants >860 tons peak capacity |  | Electric driven air-cooled plants >860 tons peak capacity
[8 empty] | Measure electric energy use and efficiency |  | Measure electric energy use and efficiency
[8 empty] | 15 minute trending |  | 15 minute trending
[8 empty] | Graphical display for hourly, daily, monthly & annual data |  | Graphical display for hourly, daily, monthly & annual data
[8 empty] | ≥36 months data storage |  | ≥36 months data storage
HVAC Construction and Insulation
Insulation for Supply & Return Ducts for Heating & Cooling, Located In
|  |  | Exterior & within building envelope separated from exterior or unconditioned space | ≥R-12 | ≥R-12 | R-12 |  | R-12 |  | R-12
|  |  | Unconditioned space & buried ducts | ≥R-6 | ≥R-6 | R-6 |  | R-6 |  | R-6
|  |  | Indirectly conditioned space |  |  |  |  | R-1.9 |  | R-1.9
Insulation for Supply & Return Ducts for Heating Only, Located In
|  |  | Exterior & within building envelope separated from exterior or unconditioned space | ≥R-12 | ≥R-12 | R-12 |  | R-12 |  | R-12
|  |  | Unconditioned space & buried ducts | ≥R-6 | ≥R-6 | R-6 |  | R-6 |  | R-6
|  |  | Indirectly conditioned space |  |  |  |  | R-1.9 |  | R-1.9
Insulation for Supply & Return Duct for Cooling Only, Located In
|  |  | Exterior & within building envelope separated from exterior or unconditioned space | ≥R-12 | ≥R-12 | R-12 |  | R-8 |  | R-8
|  |  | Unconditioned space & buried ducts | ≥R-6 | ≥R-6 | R-6 |  | R-6 |  | R-6
|  |  | Indirectly conditioned space |  |  |  |  | R-1.9 |  | R-1.9
Heating System (Steam, Steam Condensate and Hot Water) Pipe Insulation
>350ºF Fluid Temperature & 0.32 - 0.34 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 4.5" | 4.5" | 4.5" |  | 4.5" |  | 4.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 5.0" | 5.0" | 5.0" |  | 5.0" |  | 5.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 5.0" | 5.0" | 5.0" |  | 5.0" |  | 5.0"
|  |  | 4" to <8" Nominal pipe or tube size | 5.0" | 5.0" | 5.0" |  | 5.0" |  | 5.0"
|  |  | ≥8" Nominal pipe or tube size | 5.0" | 5.0" | 5.0" |  | 5.0" |  | 5.0"
251-350ºF Fluid Temperature & 0.29 - 0.32 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 3.0" | 3.0" | 3.0" |  | 3.0" |  | 3.0"
|  |  | 1" to <1.5" Nominal pipe or tube size | 4.0" | 4.0" | 4.0" |  | 4.0" |  | 4.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 4.5" | 4.5" | 4.5" |  | 4.5" |  | 4.5"
|  |  | 4" to <8" Nominal pipe or tube size | 4.5" | 4.5" | 4.5" |  | 4.5" |  | 4.5"
|  |  | ≥8" Nominal pipe or tube size | 4.5" | 4.5" | 4.5" |  | 4.5" |  | 4.5"
201-250ºF Fluid Temperature & 0.27 - 0.30 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 2.5" | 2.5" | 2.5" |  | 2.5" |  | 2.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 2.5" | 2.5" | 2.5" |  | 2.5" |  | 2.5"
|  |  | 1.5" to <4" Nominal pipe or tube size | 2.5" | 2.5" | 2.5" |  | 2.5" |  | 2.5"
|  |  | 4" to <8" Nominal pipe or tube size | 3.0" | 3.0" | 3.0" |  | 3.0" |  | 3.0"
|  |  | ≥8" Nominal pipe or tube size | 3.0" | 3.0" | 3.0" |  | 3.0" |  | 3.0"
141-200ºF Fluid Temperature & 0.25 - 0.29 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 1.5" | 1.5" | 1.5" |  | 1.5" |  | 1.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 1.5" | 1.5" | 1.5" |  | 1.5" |  | 1.5"
|  |  | 1.5" to <4" Nominal pipe or tube size | 2.0" | 2.0" | 2.0" |  | 2.0" |  | 2.0"
|  |  | 4" to <8" Nominal pipe or tube size | 2.0" | 2.0" | 2.0" |  | 2.0" |  | 2.0"
|  |  | ≥8" Nominal pipe or tube size | 2.0" | 2.0" | 2.0" |  | 2.0" |  | 2.0"
105-140ºF Fluid Temperature & 0.21 - 0.28 Insulation Conductivity (0.22 - 0.28 in ASHRAE)
|  |  | <1" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | 1" to <1.5" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 1.5" | 1.5" | 1.5" |  | 1.5" |  | 1.5"
|  |  | 4" to <8" Nominal pipe or tube size | 1.5" | 1.5" | 1.5" |  | 1.5" |  | 1.5"
|  |  | ≥8" Nominal pipe or tube size | 1.5" | 1.5" | 1.5" |  | 1.5" |  | 1.5"
Cooling Systems (Chilled Water, Brine, and Refrigerant) Pipe Insulation
40-60ºF Fluid Temperature & 0.21 - 0.27 Insulation Conductivity
|  |  | <1" Nominal pipe or tube Size | 0.5" | 0.5" | 0.5" |  | 0.5" |  | 0.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 0.5" | 0.5" | 0.5" |  | 0.5" |  | 0.5"
|  |  | 1.5" to <4" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | 4" to <8" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | ≥8" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
<40ºF Fluid Temperature & 0.20 - 0.26 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 0.5" | 0.5" | 0.5" |  | 0.5" |  | 0.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | 4" to <8" Nominal pipe or tube size | 1.0" | 1.0" | 1.0" |  | 1.0" |  | 1.0"
|  |  | ≥8" Nominal pipe or tube size | 1.5" | 1.5" | 1.5" |  | 1.5" |  | 1.5"
Sensible Panel Insulation
|  |  | Heating panel (thermally ineffective panel surfaces) | R-3.5 on all surfaces not facing space being heated | R-3.5 on all surfaces not facing space being heated | R-3.5 on all surfaces not facing space being heated |  | R-3.5 |  | R-3.5
|  |  | Radiant floor heating |  |  |  |  | R-3.5 |  | R-3.5
|  |  | Heating panels in thermal envelope separating it from exterior | ≥R-value of insulation required in opaque assembly | ≥R-value of insulation required in opaque assembly | ≥R-value of insulation required in opaque assembly |  | Adjacent envelope insulation counts toward requirement |  | Adjacent envelope insulation counts toward requirement
Duct (Ductwork and Plenum) Sealing
|  |  | Ductwork and all plenums with pressure class ratings |  |  |  |  | Seal Class A |  | Seal Class A
|  |  | Low-pressure duct systems | Fasten & seal all longitudinal and transverse joints, seams, and connections | Fasten & seal all longitudinal and transverse joints, seams, and connections | Fasten & seal all longitudinal and transverse joints, seams, and connections
|  |  | Medium-pressure duct systems | Insulate & seal all ducts and plenums | Insulate & seal all ducts and plenums | Insulate & seal all ducts and plenums
|  |  | High-pressure duct systems | Insulate & seal all ducts | Insulate & seal all ducts | Insulate & seal all ducts
Duct and Plenum Leakage Tests
|  |  | Outside ductwork |  |  |  |  | Required leakage test for all |  | Required leakage test for all
|  |  | >3 in. w.c. operating static pressure | Required leakage tests ≥25% of total duct area & documentation showing compliance submitted by designer | Required leakage tests ≥25% of total duct area & documentation showing compliance submitted by designer | Required leakage tests ≥25% of total duct area & documentation showing compliance submitted |  | Required leak tests ≥25% of total duct area selected by owner or owner representative |  | Required leak tests ≥25% of total duct area selected by owner or owner representative
|  |  |  | Air leakage rate ≤4.0 | Air leakage rate ≤4.0 | Air leakage rate ≤4.0 |  | Formula based leakage rate |  | Formula based leakage rate
Economizers
|  |  |  | Required on each cooling system (either air or water) | Either air or fluid economizer provided on: | Either air or fluid economizer provided on: |  | Required on each cooling system (either air or fluid) |  | Required on each cooling system (either air or fluid)
|  |  |  | ≥54,000 Btu/h individual fan-cooling units in buildings with other than Group R occupancy | ≥54,000 Btu/h individual fan systems in buildings with other than Group R occupancy | ≥54,000 Btu/h individual fan systems in buildings with other than Group R occupancy |  | ≥54,000 Btu/h individual fan-cooling units |  | ≥54,000 Btu/h individual fan-cooling units
|  |  |  | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤300,000 Btu/h. | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤300,000 Btu/h. | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤300,000 Btu/h in non Group R buildings |  | ≥49% unit efficiency improvement is a compliance alternative to the economizer requirement |  | ≥49% unit efficiency improvement is a compliance alternative to the economizer requirement
|  |  |  | ≥1,320,000 Btu/h total system capacity less capacity of units with air economizer of local water-cooled chilled water system | ≥1,320,000 Btu/h total system capacity less capacity of units with air economizer of local water-cooled chilled water system | ≥1,320,000 Btu/h total system capacity less capacity of units with air economizer of local water-cooled chilled water system |  | ≥1,400,000 Btu/h total chilled-water cooling system capacity |  | ≥1,400,000 Btu/h total chilled-water cooling system capacity
|  |  |  | ≥1,720,000 Btu/h total system capacity less capacity of units with air economizers of air cooled chilled water systems or district chilled water systems | ≥1,720,000 Btu/h total system capacity less capacity of units with air economizers of air cooled chilled water systems or district chilled water systems | ≥1,720,000 Btu/h total system capacity less capacity of units with air economizers of air cooled chilled water systems or district chilled water systems
|  |  |  | ≥270,000 Btu/h individual fan-cooling units in building with Group R occupancy | ≥270,000 Btu/h individual fan- systems in building with Group R occupancy | ≥270,000 Btu/h individual fan- systems in building with Group R occupancy |  | ≥270,000 Btu/h cooling systems that serve residential spaces |  | ≥270,000 Btu/h cooling systems that serve residential spaces
|  |  |  | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤1,500,000 Btu/h. | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤1,500,000 Btu/h in Group R | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤1,500,000 Btu/h in Group R
|  |  | Exceptions | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint |  | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint |  | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint
|  |  |  | Chilled-water cooling systems without a fan or use induction with capacity <1,400,000 Btu/h |  | VRF systems installed with dedicated outdoor air system |  | In hospitals & ambulatory surgery centers where 75% air supplied to spaces designed to be humidified above 35℉ dewpoint |  | In hospitals & ambulatory surgery centers where 75% air supplied to spaces designed to be humidified above 35℉ dewpoint
[8 empty] | Systems with required nonparticulate air treatment |  | Systems with required nonparticulate air treatment
|  |  |  | Expected to operate <20 hour per week | Expected to operate <20 hour per week | Expected to operate <20 hour per week |  | Expected to operate <20 hour per week |  | Expected to operate <20 hour per week
|  |  |  | Serving supermarket area with open refrigerated case work | Serving supermarket area with open refrigerated case work | Serving supermarket area with open refrigerated case work |  | Serving supermarket area with open refrigerated case work |  | Serving supermarket area with open refrigerated case work
|  |  |  | Systems with heat recovery | Systems with heat recovery | Systems with condenser heat recovery |  | Systems with condenser heat recovery |  | Systems with condenser heat recovery
[8 empty] | System's sensible cooling load at design conditions, excluding transmission & infiltration loads, is ≤ transmission & infiltration losses at 60℉ outdoor temperature |  | System's sensible cooling load at design conditions, excluding transmission & infiltration loads, is ≤ transmission & infiltration losses at 60℉ outdoor temperature
|  |  | Exceptions for computer rooms |  |  |  |  | Systems primarily serving computer rooms |  | Systems primarily serving computer rooms
[8 empty] | a) Total design cooling load of all computer rooms <3,000,000 Btu/h & building not served by central chiller plant |  | a) Total design cooling load of all computer rooms <3,000,000 Btu/h & building not served by central chiller plant
[8 empty] | b) Room design cooling load <600,000 Btu/h and building served by centralized chiller plant |  | b) Room design cooling load <600,000 Btu/h and building served by centralized chiller plant
[8 empty] | c) Cooling towers not allowed by water authority |  | c) Cooling towers not allowed by water authority
[8 empty] | d) <600,000 Btu/h computer-room cooling equipment added to existing building |  | d) <600,000 Btu/h computer-room cooling equipment added to existing building
[8 empty] | ≥75% dedicated computer room systems serve: |  | ≥75% dedicated computer room systems serve:
[8 empty] | a) Spaces classified as essential facility |  | a) Spaces classified as essential facility
[8 empty] | b) Tier IV space |  | b) Tier IV space
[8 empty] | c) Space classified as critical operations power systems |  | c) Space classified as critical operations power systems
[8 empty] | d) Spaces where core financial transactions are cleared & settled |  | d) Spaces where core financial transactions are cleared & settled
|  | Air economizer capacity |  | Outside air up to 100% of design supply air quantity | Outside air up to 100% of design supply air quantity | Outside air up to 100% of design supply air quantity |  | Outside air up to 100% of design supply air quantity |  | Outside air up to 100% of design supply air quantity
|  | Air economizer control signal |  | Sequenced with mechanical cooling equipment | Sequenced with mechanical cooling equipment | Sequenced with mechanical cooling equipment |  | Sequenced with mechanical cooling equipment |  | Sequenced with mechanical cooling equipment
|  |  |  | Not controlled by only mixed-air temperature | Not controlled by only mixed-air temperature | Not controlled by only mixed-air temperature |  | Not controlled by only mixed-air temperature |  | Not controlled by only mixed-air temperature
|  |  |  | Not increase heating energy use during normal operation | Not increase heating energy use during normal operation | Not increase heating energy use during normal operation |  | Not increase heating energy use during normal operation |  | Not increase heating energy use during normal operation
|  |  |  | Not capable of creating a false load | Not capable of creating a false load | Not capable of creating a false load |  | Not capable of creating a false load |  | Not capable of creating a false load
|  |  |  | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F |  | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F |  | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F
|  |  | Stages of mechanical cooling for direct expansion (DX) units directly controlled by space temperature | ≥2 stages for units ≥75,000 Btu/h | ≥2 stages for units ≥75,000 Btu/h | ≥2 stages for units ≥75,000 Btu/h |  | ≥2 stages for units ≥65,000 Btu/h |  | ≥2 stages for units ≥65,000 Btu/h
Direct expansion (DX) cooling stage requirements for modulating airflow units
|  |  | ≥65,000 and <240,000 Btu/h | ≥3 stages and ≤35% of full load compressor displacement | ≥3 stages and ≤35% of full load compressor displacement | ≥3 stages and ≤35% of full load compressor displacement |  | ≥3 stages and ≤35% of full load compressor displacement |  | ≥3 stages and ≤35% of full load compressor displacement
|  |  | ≥240,000 Btu/h | ≥4 stages and ≤25% of full load compressor displacement | ≥4 stages and ≤25% of full load compressor displacement | ≥4 stages and ≤25% of full load compressor displacement |  | ≥4 stages and ≤25% of full load compressor displacement |  | ≥4 stages and ≤25% of full load compressor displacement
|  |  | Air economizer high limit shutoff | Reduce outside air to minimum when it no longer reduces cooling energy usage | Reduce outside air to minimum when it no longer reduces cooling energy usage | Reduce outside air to minimum when it no longer reduces cooling energy usage |  | Reduce outside air to minimum when it no longer reduces cooling energy usage |  | Reduce outside air to minimum when it no longer reduces cooling energy usage
|  |  | Air economizer dampers (return, exhaust/relief, outdoor air) | ≤4 cfm/sf air leakage rate | ≤4 cfm/sf air leakage rate | ≤4 cfm/sf air leakage rate |  | ≤4 cfm/sf air leakage rate |  | ≤4 cfm/sf air leakage rate
|  |  | Preheat coils |  |  |  |  | Prevent heat output during mechanical cooling including economizer operation |  | Prevent heat output during mechanical cooling including economizer operation
|  | Water economizer |  | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb |  | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb |  | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb
|  |  |  | Define exceptions for computer rooms with other economizers |  | Define exceptions for computer rooms with other economizers |  | Define exceptions for computer rooms with other economizers |  | Define exceptions for computer rooms with other economizers
[6 empty] | Required for systems (required to have economizer) with dehumidification where 100% of cooling load can be met with water-cooled fluid economizer when outside air 50ºF db/45ºF wb |  | Required for systems (required to have economizer) with dehumidification where 100% of cooling load can be met with water-cooled fluid economizer when outside air 45ºF db/40ºF wb |  | Required for systems (required to have economizer) with dehumidification where 100% of cooling load can be met with water-cooled fluid economizer when outside air 45ºF db/40ºF wb
|  |  | Water economizer pressure drop | <15 ft. or secondary loop | <15 ft. or secondary loop | <15 ft. or secondary loop |  | <15 ft. or secondary loop |  | <15 ft. or secondary loop
|  |  | Water economizer control | Integrated with mechanical equipment to provide partial cooling | Integrated with mechanical equipment to provide partial cooling | Integrated with mechanical equipment to provide partial cooling |  | Integrated with mechanical equipment to provide partial cooling |  | Integrated with mechanical equipment to provide partial cooling
Economizer Fault Detection and Diagnostics (FDD)
|  |  | Air-cooled unitary direct-expansion units with required economizer | Outside, supply and return air sensors | Outside, supply and return air sensors | Outside, supply and return air sensors |  | Outside, supply and return air sensors |  | Outside, supply and return air sensors
|  |  |  | System status indication | System status indication | Display value of each sensor and system status |  | Display value of each sensor and system status |  | Display value of each sensor and system status
|  |  |  | Capable of manual operation for independent testing & verification | Capable of manual operation for independent testing & verification | Capable of manual operation for independent testing & verification |  | Capable of manual operation for independent testing & verification |  | Capable of manual operation for independent testing & verification
|  |  |  | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats |  | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats |  | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats
|  |  |  | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air. | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air. | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air. |  | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air. |  | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air.
Simultaneous Heating and Cooling Limitation
|  | Zone thermostatic controls |  | Configure controls to prevent simultaneous operation & to maintain deadband where separate heating & cooling controls are provided | Configure controls to prevent simultaneous operation & to maintain deadband where separate heating & cooling controls are provided | Prevent reheating, recooling and mixing or simultaneously supplying air that has been previously heated or cooled |  | Prevent reheating, recooling and mixing or simultaneously supplying air that has been previously heated or cooled |  | Prevent reheating, recooling and mixing or simultaneously supplying air that has been previously heated or cooled
|  |  | VAV control requirement before reheating, recooling or mixing takes place | Choose one of: | Choose one of: | Choose one of: |  | Exception: |  | Exception:
|  |  |  | 1) 30% of maximum supply air to each zone | 1) 30% of maximum supply air to each zone without DDC | 1) 30% of maximum supply air to each zone without DDC |  | Zone air flow <larger of: |  | Zone air flow <larger of:
|  |  |  | 2) ≤300 cfm where maximum flow rate <10% of total system supply airflow rate | 2) 20% of maximum supply air to each zone with DDC where | 2) 20% of maximum supply air to each zone with DDC where |  | a) 20% of maximum supply air to each zone with DDC; 30% for other systems |  | a) 30% of maximum supply air to each zone for systems without DDC
|  |  |  | 3) Minimum ventilation requirements | Airflow in first stage of heating is deadband flow rate | Airflow in first stage of heating is deadband flow rate |  | b) Minimum ventilation requirements |  | b) Minimum primary airflow rate to meet ventilation requirements for systems with DDC
|  |  |  | 4) Any higher rate demonstrated to reduce overall system annual energy use | Airflow in second stage of heating <50% zone design peak supply rate | Airflow in second stage of heating <50% zone design peak supply rate |  | c) Any higher rate demonstrated to reduce overall system annual energy use |  | c) Any higher rate demonstrated to reduce overall system annual energy use
|  |  |  | 5) Airflow rate required to comply with applicable code or accreditation standards | 3) Minimum ventilation requirements | 3) Minimum ventilation requirements |  | d) Airflow rate required to comply with applicable code or accreditation standards |  | d) Airflow rate required to comply with applicable code or accreditation standards
[5 empty] | 4) Any higher rate demonstrated to reduce overall system annual energy use | 4) Any higher rate demonstrated to reduce overall system annual energy use |  | Exception: |  | Exception:
[5 empty] | 5) Airflow rate required to comply with applicable code or accreditation standards | 5) Airflow rate required to comply with applicable code or accreditation standards |  | Zones with DDC, comply with all of: |  | Zones with DDC, comply with all of:
[8 empty] | 1) Airflow rate in dead band does not exceed larger of: |  | 1) Airflow rate in dead band does not exceed larger of:
[8 empty] | 1a) 20% zone design peak supply rate |  | 1a) Minimum primary airflow rate
[8 empty] | 1b) Minimum ventilation requirements |  | 1b) Higher rate demonstrated to reduce overall system annual energy use
[8 empty] | 1c) Any higher rate demonstrated to reduce overall system annual energy use |  | 1c) Airflow rate required to comply with applicable code or accreditation standards
1d) Airflow rate required to comply with applicable code or accreditation standards
[8 empty] | 2) Reheated, recooled or mixed air flow rate <50% zone design peak supply rate |  | 2) Reheated, recooled or mixed air flow rate <50% zone design peak supply rate
[8 empty] | 3) First stage of heating modulates zone supply air temperature to maximum setpoint while airflow is maintained at dead band flow rate |  | 3) First stage of heating modulates zone supply air temperature to maximum setpoint while airflow is maintained at dead band flow rate
[8 empty] | 4) Second stage of heating modulates airflow rate to heating maximum flow rate |  | 4) Second stage of heating modulates airflow rate to heating maximum flow rate
Exception:
1) Compliant laboratory exhaust system
2) Zones where ≥75% energy for reheating or for providing warm air in mixing system is provided from site-recovered energy or site-solar energy
|  | Supply air temperature reheat limit | [5 empty] | Where allowed and duct openings are >6' above floor, supply air temperature ≤20º space temperature setpoint, except during warm-up |  | Where allowed and duct openings are >6' above floor, supply air temperature ≤20º space temperature setpoint, except during warm-up
Hydronic system controls
|  |  | Three-pipe systems | Prohibited | Prohibited | Prohibited |  | Prohibited |  | Prohibited
|  |  | Two-pipe changeover systems | ≥15º F outside air temperature changeover deadband | ≥15º F outside air temperature changeover deadband | ≥15º F outside air temperature changeover deadband |  | ≥15º F outside air temperature changeover deadband |  | ≥15º F outside air temperature changeover deadband
|  |  |  | 4 hour minimum operations in one mode | 4 hour minimum operations in one mode | 4 hour minimum operations in one mode |  | 4 hour minimum operations in one mode |  | 4 hour minimum operations in one mode
|  |  |  | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart |  | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart |  | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart
|  |  | Hydronic (water loop) heat pump systems | ≥20ºF deadband between rejection and addition | ≥20ºF deadband between rejection and addition | ≥20ºF deadband between heat rejection and heat addition |  | ≥20ºF deadband between heat rejection and heat addition |  | ≥20ºF deadband between heat rejection and heat addition
|  |  |  | Where open- or closed-circuit tower is used, provide separate heat exchanger to isolate tower loop from heat pump loop and automatic valve on tower loop; control heat loss by shutting down tower pump and closing valve | If closed-circuit tower, use either: | If closed-circuit tower, use either: |  | If closed-circuit tower, use either: |  | If closed-circuit tower, use either:
[5 empty] | Automatic valve to bypass all but minimal flow around tower or | Automatic valve to bypass all but minimal flow around tower or |  | Automatic valve to bypass all but minimal flow around tower or |  | Automatic valve to bypass all but minimal flow around tower or
[5 empty] | low-leakage positive closure dampers | low-leakage positive closure dampers |  | low-leakage positive closure dampers |  | low-leakage positive closure dampers
[5 empty] | If open-circuit tower, Automatic valve to bypass all water flow around tower | If open-circuit tower, Automatic valve to bypass all water flow around tower |  | If open-circuit tower, Automatic valve to bypass all water flow around tower |  | If open-circuit tower, Automatic valve to bypass all water flow around tower
[5 empty] | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop | If cooling tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop |  | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop |  | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop
|  |  |  | Two-position valves on each heat pump on systems with total pump system power >10 hp | Two-position valves on each heat pump on systems with total pump system power >10 hp | Two-position valves on each heat pump on systems with total pump system power >10 hp |  | Two-position valves on each hydronic heat pump or water-cooled air conditioner |  | Two-position valves on each hydronic heat pump or water-cooled air conditioner
|  |  | Hydronic heat pump & water -cooled unitary air conditioners |  |  |  |  | Speed control or device that results ≤30% design wattage at 50% design flow when total pump system power >5 hp |  | Speed control or device that results ≤30% design wattage at 50% design flow when total pump system power >5 hp
|  |  | Hydronic variable flow | Chilled- or hot-water systems ≥500,000 Btu/h output capacity shall | Chilled- or hot-water systems ≥300,000 Btu/h output capacity shall | Chilled- or hot-water systems ≥300,000 Btu/h design output capacity shall |  | On chilled- & hot-water distribution systems ≥3 control valves |  | On chilled- & hot-water distribution systems ≥3 control valves
|  |  |  | Automatically reset supply-water temperature | Automatically reset supply-water temperature | Automatically reset supply-water temperature |  | Speed control or device that results ≤30% design wattage at 50% design flow when individual or combined parallel pumps ≥7.5 hp |  | Speed control or device that results ≤30% design wattage at 50% design flow when individual or combined parallel pumps ≥7.5 hp
|  |  |  | Automatically vary flow on systems with total system pump capacity ≥10 hp with ≥3 control valves | Automatically vary flow on systems with total system pump capacity ≥2 hp with ≥3 control valves | Automatically vary flow on systems with total system pump capacity ≥2 hp with ≥3 control valves
[5 empty] | Continuously operating chilled- & hot-water pumps & heat rejection loop pumps ≥2 hp have variable speed drives | Continuously operating chilled- & hot-water pumps & heat rejection loop pumps ≥2 hp have variable speed drives
[5 empty] | DDC configured chilled- & hot-water pumps & heat rejection loop pumps ≥7.5 hp have variable speed drives | DDC configured chilled- & hot-water pumps & heat rejection loop pumps ≥7.5 hp have variable speed drives
[5 empty] | Speed control or device that results ≤30% design wattage at 50% design flow with ≥1 control valve nearly wide open | Speed control or device that results ≤30% design wattage at 50% design flow with ≥1 control valve nearly wide open
Humidifier preheat
|  |  | Preheating jackets mounted in airstream |  |  |  |  | Automatic shutoff valve |  | Automatic shutoff valve
|  |  | Dispersion tube hot surface in airstream |  |  |  |  | ≥R-0.5 insulation |  | ≥R-0.5 insulation
|  | Preheat coils | [7 empty] | Stop output during mechanical cooling and economizer operation
Air System Design and Control
|  | Fan power limitation |  | Fan systems >5 hp | Fan systems >5 hp | Fan systems >5 hp |  | Fan systems >5 hp |  | Fan systems >5 hp
Option 1: Fan system motor nameplate hp
|  |  | Constant volume | hp ≤CFMs x 0.0011 | hp ≤CFMs x 0.0011 | hp ≤CFMs x 0.0011 |  | hp ≤CFMs x 0.0011 |  | hp ≤CFMs x 0.0011
|  |  | Variable volume | hp ≤CFMs x 0.0015 | hp ≤CFMs x 0.0015 | hp ≤CFMs x 0.0015 |  | hp ≤CFMs x 0.0015 |  | hp ≤CFMs x 0.0015
Option 2: Fan system bhp
|  |  | Constant volume | bhp ≤CFMs x 0.00094 + A | bhp ≤CFMs x 0.00094 + A | bhp ≤CFMs x 0.00094 + A |  | bhp ≤CFMs x 0.00094 + A |  | bhp ≤CFMs x 0.00094 + A
|  |  | Variable volume | bhp ≤CFMs x 0.0013 + A | bhp ≤CFMs x 0.0013 + A | bhp ≤CFMs x 0.0013 + A |  | bhp ≤CFMs x 0.0013 + A |  | bhp ≤CFMs x 0.0013 + A
|  |  | Single zone variable air volume | Comply with constant volume fan power limitation | Comply with constant volume fan power limitation | Comply with constant volume fan power limitation |  | Comply with constant volume fan power limitation |  | Comply with constant volume fan power limitation
|  |  | Air systems with required air treatment or filtering, or heat recovery, or direct evaporation | Device adjustment tables | Device adjustment tables | Device adjustment tables |  | Device adjustment tables |  | Device adjustment tables
Motor Nameplate Horsepower
|  |  | For each fan | Fan brake horsepower indicated on construction documents | Fan brake horsepower indicated on construction documents | Fan brake horsepower indicated on construction documents |  | Fan brake horsepower indicated on construction documents |  | Fan brake horsepower indicated on construction documents
|  |  |  | Selected motor not larger than first available motor size greater than | Selected motor not larger than first available motor size greater than | Selected motor not larger than first available motor nameplate rating greater than |  | Selected motor not larger than first available motor nameplate rating greater than |  | Selected motor not larger than first available motor nameplate rating greater than
|  |  |  | 1) 1.5 x fan bhp for fans <6 bhp | 1) 1.5 x fan bhp for fans <6 bhp | 1) 1.5 x fan bhp for fans <6 bhp |  | 1) 1.5 x fan bhp for fans <6 bhp |  | 1) 1.5 x fan bhp for fans <6 bhp
|  |  |  | 2) 1.3 x fan bhp for fans ≥6 bhp | 2) 1.3 x fan bhp for fans ≥6 bhp | 2) 1.3 x fan bhp for fans ≥6 bhp |  | 2) 1.3 x fan bhp for fans ≥6 bhp |  | 2) 1.3 x fan bhp for fans ≥6 bhp
|  |  |  | 3)Systems complying with fan power limitation Option 1 | 3)Systems complying with fan power limitation Option 1 | 3)Systems complying with fan power limitation Option 1 |  | 3)Systems complying with fan power limitation Option 1 |  | 3)Systems complying with fan power limitation Option 1
Fan efficiency
|  |  | Fan energy index (FEI) |  |  | Each fan & fan array |  |  |  | Each fan & fan array
|  |  | Constant volume system |  |  | ≥1.0 |  |  |  | ≥1.0
|  |  | Variable-air-volume system |  |  | ≥0.95 |  |  |  | ≥0.95
|  |  | Fan efficiency grade (FEG) | ≥67 | ≥67 |  |  | ≥67
|  |  | Total efficiency of fan @ design point of operation | Within 15% points of maximum total efficiency of the fan | Within 15% points of maximum total efficiency of the fan |  |  | Within 15% points of maximum total efficiency of the fan
|  | Fractional hp fan motors |  | ≥1/12 hp and <1 hp | ≥1/12 hp and <1 hp | ≥1/12 hp and <1 hp |  | ≥1/12 hp and <1 hp |  | ≥1/12 hp and <1 hp
|  |  |  | Electronically commutated motors or | Electronically commutated motors or | Electronically commutated motors or |  | Electronically commutated motors or |  | Electronically commutated motors or
|  |  |  | ≥70% motor efficiency | ≥70% motor efficiency | ≥70% motor efficiency |  | ≥70% motor efficiency |  | ≥70% motor efficiency
|  |  |  | Have means to adjust speed for either balancing or remote control | Have means to adjust speed for either balancing or remote control | Have means to adjust speed for either balancing or remote control |  | Have means to adjust speed for either balancing or remote control |  | Have means to adjust speed for either balancing or remote control
Low-capacity ventilation fan efficacy
|  |  | HRV or ERV |  |  | 1.2 cfm/watt
|  |  | In-line fan |  |  | 3.8 cfm/watt
|  |  | Bathroom, utility fan <90 cfm |  |  | 2.8 cfm/watt
|  |  | Bathroom, utility fan ≥90 cfm |  |  | 3.5 cfm/watt
Fan airflow control
|  |  | Supply air systems serving multiple zones | VAV required | VAV required | VAV required
|  |  | Cooling systems required to vary air flow as function of load | For DX cooling system | For DX cooling system | For DX cooling system |  | For DX cooling system |  | For DX cooling system
|  |  |  | ≥65,000 Btu/h mechanical cooling capacity | ≥65,000 Btu/h mechanical cooling capacity | ≥65,000 Btu/h mechanical cooling capacity |  | ≥65,000 Btu/h mechanical cooling capacity |  | ≥65,000 Btu/h mechanical cooling capacity
|  |  |  | For chilled water and evaporative cooling systems | For chilled water and evaporative cooling systems | For chilled water and evaporative cooling systems |  | For chilled water and evaporative cooling systems |  | For chilled water and evaporative cooling systems
|  |  |  | ≥¼ hp fan motor | ≥¼ hp fan motor | ≥¼ hp fan motor |  | ≥¼ hp fan motor |  | ≥¼ hp fan motor
|  |  | Fan control for units that control mechanical cooling based on space temperature | ≥2 stages | ≥2 stages | ≥2 stages |  | ≥2 stages |  | ≥2 stages
|  |  |  | Low or minimum speed ≤66% of full speed | Low or minimum speed ≤66% of full speed | Low or minimum speed ≤66% of full speed |  | Low or minimum speed ≤66% of full speed |  | Low or minimum speed ≤66% of full speed
|  |  |  | Power draw at low or minimum speed ≤40% power at full speed | Power draw at low or minimum speed ≤40% power at full speed | Power draw at low or minimum speed ≤40% power at full speed |  | Power draw at low or minimum speed ≤40% power at full speed |  | Power draw at low or minimum speed ≤40% power at full speed
|  |  |  | Low or minimum speed used during low cooling load and ventilation-only operation | Low or minimum speed used during low cooling load and ventilation-only operation | Low or minimum speed used during low cooling load and ventilation-only operation |  | Low or minimum speed used during low cooling load and ventilation-only operation |  | Low or minimum speed used during low cooling load and ventilation-only operation
|  |  | Fan control for units that control space temperature by modulating airflow | Minimum speed ≤50% full speed | Minimum speed ≤50% full speed | Minimum speed ≤50% full speed |  | Minimum speed ≤50% full speed |  | Minimum speed ≤50% full speed
|  |  |  | Power draw at minimum speed ≤30% power at full speed | Power draw at minimum speed ≤30% power at full speed | Power draw at minimum speed ≤30% power at full speed |  | Power draw at minimum speed ≤30% power at full speed |  | Power draw at minimum speed ≤30% power at full speed
|  |  |  | Minimum speed used during low cooling load and ventilation-only operation | Minimum speed used during low cooling load and ventilation-only operation | Minimum speed used during low cooling load and ventilation-only operation |  | Minimum speed used during low cooling load and ventilation-only operation |  | Minimum speed used during low cooling load and ventilation-only operation
|  |  | Fan control for units with airside economizer | ≥2 speeds during economizer operation | ≥2 speeds during economizer operation | ≥2 speeds during economizer operation |  | ≥2 speeds during economizer operation |  | ≥2 speeds during economizer operation
Variable air volume (VAV) fan control
|  |  | Static pressure reset | For systems with direct digital control of individual zone boxes | For systems with direct digital control of individual zone boxes | For systems with direct digital control of individual zone boxes |  | For systems with total fan system ≥5 hp and direct digital control of individual zone boxes |  | For systems with total fan system ≥5 hp and direct digital control of individual zone boxes
|  |  |  | Control Capable of: | Control Capable of: | Control Capable of: |  | Control Capable of: |  | Control Capable of:
|  |  |  | 1) Automatic detection of any zone that excessively drives reset logic | 1) Automatic detection of any zone that excessively drives reset logic | 1) Automatic detection of any zone that excessively drives reset logic |  | 1) Monitor zone damper positions or other static pressure indicator |  | 1) Monitor zone damper positions or other static pressure indicator
|  |  |  | 2) Generating alarm | 2) Generating alarm | 2) Generating alarm |  | 2) Automatic detection of any zone that excessively drives reset logic & generating alarm |  | 2) Automatic detection of any zone that excessively drives reset logic & generating alarm
|  |  |  | 3) Allow operator to remove zone(s) from reset algorithm | 3) Allow operator to remove zone(s) from reset algorithm | 3) Allow operator to remove zone(s) from reset algorithm |  | 3) Allow operator to remove zone(s) from reset algorithm |  | 3) Allow operator to remove zone(s) from reset algorithm
|  |  | Return and relief fan control |  |  |  |  | Controlled to maintain building pressure |  | Controlled to maintain building pressure
[8 empty] | Variable speed fans or other devices resulting in total return/relief fan system demand ≤30% total design power @ 50% total design fan flow |  | Variable speed fans or other devices resulting in total return/relief fan system demand ≤30% total design power @ 50% total design fan flow
|  |  | Ventilation optimization control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control |  | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control |  | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control
|  |  | Parallel-flow fan-powered VAV terminal control |  | Turn off terminal fan except when required for space heating or for ventilation | Turn off terminal fan except when required for space heating or for ventilation |  | Turn off terminal fan except when required for space heating or for ventilation |  | Turn off terminal fan except when required for space heating or for ventilation
[5 empty] | Turn on terminal fan as first stage heating before heating coil activation | Turn on terminal fan as first stage heating before heating coil activation |  | Turn on terminal fan as first stage heating before heating coil activation |  | Turn on terminal fan as first stage heating before heating coil activation
[5 empty] | During warmup or setback temperature control either | During warmup or setback temperature control either |  | During warmup or setback temperature control either |  | During warmup or setback temperature control either
[5 empty] | Operate terminal fan & heating coil without primary air or | Operate terminal fan & heating coil without primary air or |  | Operate terminal fan & heating coil without primary air or |  | Operate terminal fan & heating coil without primary air or
[5 empty] | Reverse terminal damper logic and heat with primary air | Reverse terminal damper logic and heat with primary air |  | Reverse terminal damper logic and heat with primary air |  | Reverse terminal damper logic and heat with primary air
|  |  | Supply-air temperature reset | Required for multiple zone HVAC systems | Required for multiple zone HVAC systems | Required for multiple zone HVAC systems |  | Required for Multiple Zone HVAC Systems |  | Required for Multiple Zone HVAC Systems
Ventilation design
[8 empty] | Design minimum system outdoor air ≤135% required minimum outdoor rate |  | Design minimum system outdoor air ≤135% required minimum outdoor rate
[8 empty] | Control to supply no more than required minimum outdoor rate with single set-point adjustment |  | Control to supply no more than required minimum outdoor rate with single set-point adjustment
[8 empty] | System includes required exhaust air energy recovery |  | System includes required exhaust air energy recovery
|  | Occupied-standby controls | [7 empty] | For zones serving rooms with required automatic partial off or automatic full off lighting controls
Within 5 minutes of entering in occupied-standby mode shall:
Activate ≥1℉ heating set point setback
Activate ≥1℉ cooling set point setup
Shut off supply airflow when space temperature between active heating & cooling set points
Hydronic System Design and Control
Part load hydronic system controls
|  |  | Automatic supply water temperature reset on chilled or heated water systems for comfort conditioning control | Systems ≥500,000 Btu/h | Systems ≥300,000 Btu/h | Systems ≥300,000 Btu/h |  | Systems ≥300,000 Btu/h |  | Systems ≥300,000 Btu/h
|  |  |  | Required | Required | Required |  | Required |  | Required
|  |  | Variable fluid flow control | Automatically vary fluid flow ≥50% on systems with combined motor capacity ≥10 hp and with ≥3 control valves | Automatically vary fluid flow ≥50% on systems with combined motor capacity ≥2 hp and with ≥3 control valves | Automatically vary fluid flow ≥50% on systems with combined motor capacity ≥2 hp and with ≥3 control valves |  | Automatically vary fluid flow ≤25% design flow rate or to minimum required flow rate for proper operation of system |  | Automatically vary fluid flow ≤25% design flow rate or to minimum required flow rate for proper operation of system
[5 empty] | ≥50% on heating-water systems, chilled water systems and heat rejection loops serving water cooled unitary air conditioners with combined motor capacity ≥2 hp | ≥50% on heating-water systems, chilled water systems and heat rejection loops serving water cooled unitary air conditioners with combined motor capacity ≥2 hp |  |  |  | Controls or devices result in pump demand ≤30% design wattage at 50% design water flow
|  |  |  | ≥50% on chilled water systems and heat rejection loops serving water cooled unitary air conditioners with combined motor capacity ≥10 hp | Controls or devices result in pump demand ≤30% design wattage at 50% design water flow | Controls or devices result in pump demand ≤30% design wattage at 50% design water flow |  | Controls or devices result in pump demand ≤30% design wattage at 50% design water flow
|  |  | Variable flow systems | Speed control or multi-staged pumps | Speed control on pumps ≥7.5 hp | Speed control on pumps ≥7.5 hp |  | On distribution systems with ≥3 control valves and total nameplate horsepower ≥7.5 hp |  | On distribution systems with ≥3 control valves and total nameplate horsepower ≥7.5 hp
|  |  | Equipment isolation | Automatically reduce flow through chiller/boiler when chiller/boiler is shut down | Automatically reduce flow through chiller/boiler when chiller/boiler is shut down | Automatically reduce flow through chiller/boiler when chiller/boiler is shut down |  | Automatically shut off flow through chiller/boiler when chiller/boiler is shut down |  | Automatically shut off flow through chiller/boiler when chiller/boiler is shut down
|  |  | Boiler Controls | Automatic controls to sequence operations on multi-packaged boiler system | Automatic controls to sequence operations on multi-packaged boiler system | Boiler systems design input ≥1,000,000 Btu/h |  | Boiler systems design input ≥1,000,000 Btu/h |  | Boiler systems design input ≥1,000,000 Btu/h
|  |  |  | Multistage or modulating burner on single boiler systems ≥500,000 Btu/h | Multistage or modulating burner on single boiler systems ≥500,000 Btu/h | Turndown achieved with multiple single boilers and/or modulating boilers |  | Turndown achieved with multiple single boilers and/or modulating boilers |  | Turndown achieved with multiple single boilers and/or modulating boilers
|  |  |  | Minimum boiler system turndown ratios | Minimum boiler system turndown ratios | Minimum boiler system turndown ratios |  | Minimum boiler system turndown ratios |  | Minimum boiler system turndown ratios
|  |  |  | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h |  | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h |  | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h
|  |  |  | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h |  | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h |  | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h
|  |  |  | 5 to 1 on >10,000,000 Btu/h | 5 to 1 on >10,000,000 Btu/h | 5 to 1 on >10,000,000 Btu/h |  | 5 to 1 on >10,000,000 Btu/h |  | 5 to 1 on >10,000,000 Btu/h
|  | Chilled-water coil selection | [5 empty] | ≥15℉ temperature differential |  | ≥15℉ temperature differential
[8 empty] | ≥57℉ leaving water temperature @ design conditions |  | ≥57℉ leaving water temperature @ design conditions
Chilled water and condenser water pipe sizing
|  |  | Nominal size (inches) |  |  |  |  | Maximum design flow |  | Maximum design flow
|  |  | ≤2,000 operating hours per year, |  |  |  |  | Variable flow/variable speed | Other | Variable flow/variable speed | Other
|  |  | 2.5" |  |  |  |  | 180 gpm | 120 gpm | 180 gpm | 120 gpm
|  |  | 3" |  |  |  |  | 270 gpm | 180 gpm | 270 gpm | 180 gpm
|  |  | 4" |  |  |  |  | 530 gpm | 350 gpm | 530 gpm | 350 gpm
|  |  | 5" |  |  |  |  | 620 gpm | 410 gpm | 620 gpm | 410 gpm
|  |  | 6" |  |  |  |  | 1100 gpm | 740 gpm | 1100 gpm | 740 gpm
|  |  | 8" |  |  |  |  | 1800 gpm | 1200 gpm | 1800 gpm | 1200 gpm
|  |  | 10" |  |  |  |  | 2700 gpm | 1800 gpm | 2700 gpm | 1800 gpm
|  |  | 12" |  |  |  |  | 3800 gpm | 2500 gpm | 3800 gpm | 2500 gpm
|  |  | >12" |  |  |  |  | 13.0 fps | 8.5 fps | 13.0 fps | 8.5 fps
|  |  | >2,000 and ≤4,400 operating hours per year, |  |  |  |  | Variable flow/variable speed | Other | Variable flow/variable speed | Other
|  |  | 2.5" |  |  |  |  | 130 gpm | 85 gpm | 130 gpm | 85 gpm
|  |  | 3" |  |  |  |  | 210 gpm | 140 gpm | 210 gpm | 140 gpm
|  |  | 4" |  |  |  |  | 400 gpm | 260 gpm | 400 gpm | 260 gpm
|  |  | 5" |  |  |  |  | 470 gpm | 310 gpm | 470 gpm | 310 gpm
|  |  | 6" |  |  |  |  | 860 gpm | 570 gpm | 860 gpm | 570 gpm
|  |  | 8" |  |  |  |  | 1400 gpm | 900 gpm | 1400 gpm | 900 gpm
|  |  | 10" |  |  |  |  | 2000 gpm | 1300 gpm | 2000 gpm | 1300 gpm
|  |  | 12" |  |  |  |  | 2900 gpm | 1900 gpm | 2900 gpm | 1900 gpm
|  |  | >12" |  |  |  |  | 9.5 fps | 6.5 fps | 9.5 fps | 6.5 fps
|  |  | >4,400 operating hours per year |  |  |  |  | Variable flow/variable speed | Other | Variable flow/variable speed | Other
|  |  | 2.5" |  |  |  |  | 110 gpm | 68 gpm | 110 gpm | 68 gpm
|  |  | 3" |  |  |  |  | 170 gpm | 110 gpm | 170 gpm | 110 gpm
|  |  | 4" |  |  |  |  | 320 gpm | 210 gpm | 320 gpm | 210 gpm
|  |  | 5" |  |  |  |  | 370 gpm | 250 gpm | 370 gpm | 250 gpm
|  |  | 6" |  |  |  |  | 680 gpm | 440 gpm | 680 gpm | 440 gpm
|  |  | 8" |  |  |  |  | 1100 gpm | 700 gpm | 1100 gpm | 700 gpm
|  |  | 10" |  |  |  |  | 1600 gpm | 1000 gpm | 1600 gpm | 1000 gpm
|  |  | 12" |  |  |  |  | 2300 gpm | 1500 gpm | 2300 gpm | 1500 gpm
|  |  | >12" |  |  |  |  | 7.5 fps | 5.0 fps | 7.5 fps | 5.0 fps
|  | Buildings with High-Capacity Space-Heating Gas Boiler Systems | [7 empty] | New buildings with ≥1,000,000 & ≤10,000,000,Btu/h hot-water systems for space heating
|  |  | Thermal efficiency (Et) | [6 empty] | ≥90% or capacity weighted average ≥90%
|  |  | Distribution system design | [6 empty] | ≤120℉ return water temperature to boiler
Recirculates or bypasses ≤20% design flow
Heat Rejection Equipment
|  |  | Fan speed control |  | Individual motor or | Individual motor or |  | Individual motor or |  | Individual motor or
|  |  |  | Each fan ≥7.5 hp | array of motors ≥5 hp | array of motors ≥5 hp |  | array of motors ≥5 hp |  | array of motors ≥5 hp
|  |  | Multiple-cell equipment with variable speed fans | Operate maximum number of fans that comply with manufacturer's requirements for all components | Operate maximum number of fans that comply with manufacturer's requirements for all components | Operate maximum number of fans that comply with manufacturer's requirements for all components |  | Operate maximum number of fans that comply with manufacturer's requirements for all components |  | Operate maximum number of fans that comply with manufacturer's requirements for all components
|  |  |  | Operate all fans at same speed | Operate all fans at same speed | Operate all fans at same speed |  | Operate all fans at same speed |  | Operate all fans at same speed
|  |  | Limitation on centrifugal fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers |  | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers |  | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers
|  |  | Tower fan turndown | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell |  | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell |  | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell
Energy Recovery
|  |  | Nontransitory dwelling units exhaust air energy recovery |  |  | Provide system resulting in ≥60% enthalpy recovery ratio at heating design conditions |  |  |  | Provide system resulting in ≥60% enthalpy recovery ratio at heating design conditions
|  |  | Energy recovery ventilation system (Spaces other than nontransitory dwelling unit exhaust air energy recovery) | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air |  | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air |  | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air
|  |  |  | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate) | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate) | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate) |  | For each fan system based on outdoor air percentage of full design flow (Exception: where sum of exhaust & relieved airflow rates within 20 ft of each other < 75% of design outdoor air flow rate excluding exhaust air) |  | For each fan system based on outdoor air percentage of full design flow (Exception: where sum of exhaust & relieved airflow rates within 20 ft of each other < 75% of design outdoor air flow rate excluding exhaust air)
|  |  |  | Provisions to bypass or control energy recovery system to permit air economizer operation | Provisions to bypass or control energy recovery system to permit air economizer operation | Provisions to bypass or control energy recovery system to permit air economizer operation |  | Provisions to bypass or control energy recovery system to permit air economizer operation |  | Provisions to bypass or control energy recovery system to permit air economizer operation
|  |  |  | On systems operating <8,000 hours per year | On systems operating <8,000 hours per year | On systems operating <8,000 hours per year |  | On systems operating <8,000 hours per year |  | On systems operating <8,000 hours per year
|  |  | % outdoor air at full design airflow rate | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate |  | Required for Systems with Design Supply Fan Flow Rate |  | Required for Systems with Design Supply Fan Flow Rate
|  |  | ≥10% & <20% | ≥26,000 cfm | ≥26,000 cfm | ≥26,000 cfm |  | ≥26,000 cfm |  | ≥26,000 cfm
|  |  | ≥20% & <30% | ≥16,000 cfm | ≥16,000 cfm | ≥16,000 cfm |  | ≥16,000 cfm |  | ≥16,000 cfm
|  |  | ≥30% & <40% | ≥5,500 cfm | ≥5,500 cfm | ≥5,500 cfm |  | ≥5,500 cfm |  | ≥5,500 cfm
|  |  | ≥40% & <50% | ≥4,500 cfm | ≥4,500 cfm | ≥4,500 cfm |  | ≥4,500 cfm |  | ≥4,500 cfm
|  |  | ≥50% & <60% | ≥3,500 cfm | ≥3,500 cfm | ≥3,500 cfm |  | ≥3,500 cfm |  | ≥3,500 cfm
|  |  | ≥60% & <70% | ≥2,000 cfm | ≥2,000 cfm | ≥2,000 cfm |  | ≥2,000 cfm |  | ≥2,000 cfm
|  |  | ≥70% & <80% | ≥1,000 cfm | ≥1,000 cfm | ≥1,000 cfm |  | ≥1,000 cfm |  | ≥1,000 cfm
|  |  | ≥80% | ≥0 cfm | ≥0 cfm | ≥120 cfm |  | ≥120 cfm |  | ≥120 cfm
|  |  |  | Required on all systems operating ≥8,000 hours per year | Required on all systems operating ≥8,000 hours per year | On systems operating ≥8,000 hours per year |  | On systems operating ≥8,000 hours per year |  | On systems operating ≥8,000 hours per year
|  |  | % outdoor air at full design airflow rate |  | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate |  | Required for Systems with Design Supply Fan Flow Rate |  | Required for Systems with Design Supply Fan Flow Rate
|  |  | ≥10% & <20% |  | ≥200 cfm | ≥200 cfm |  | ≥200 cfm |  | ≥200 cfm
|  |  | ≥20% & <30% |  | ≥130 cfm | ≥130 cfm |  | ≥130 cfm |  | ≥130 cfm
|  |  | ≥30% & <40% |  | ≥100 cfm | ≥100 cfm |  | ≥100 cfm |  | ≥100 cfm
|  |  | ≥40% & <50% |  | ≥80 cfm | ≥80 cfm |  | ≥80 cfm |  | ≥80 cfm
|  |  | ≥50% & <60% |  | ≥70 cfm | ≥70 cfm |  | ≥70 cfm |  | ≥70 cfm
|  |  | ≥60% & <70% |  | ≥60 cfm | ≥60 cfm |  | ≥60 cfm |  | ≥60 cfm
|  |  | ≥70% & <80% |  | ≥50 cfm | ≥50 cfm |  | ≥50 cfm |  | ≥50 cfm
|  |  | ≥80% |  | ≥40 cfm | ≥40 cfm |  | ≥40 cfm |  | ≥40 cfm
|  |  | Heat recovery for service water heating | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load |  | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load |  | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load
|  |  |  | Capacity to provide smaller of | Capacity to provide smaller of | Capacity to provide smaller of |  | Capacity to provide smaller of |  | Capacity to provide smaller of
|  |  |  | 1) 60% peak heat rejection load at design conditions | 1) 60% peak heat rejection load at design conditions | 1) 60% peak heat rejection load at design conditions |  | 1) 60% peak heat rejection load at design conditions |  | 1) 60% peak heat rejection load at design conditions
|  |  |  | 2) Preheating required to raise peak service hot water draw to 85°F | 2) Preheating required to raise peak service hot water draw to 85°F | 2) Preheating required to raise peak service hot water draw to 85°F |  | 2) Preheating required to raise peak service hot water draw to 85°F |  | 2) Preheating required to raise peak service hot water draw to 85°F
|  |  | Heat recovery for space conditioning | [6 empty] | Required for acute inpatient hospital, where building or portion of building used 24 hours a day for inpatient medical, obstetric or surgical care
Total design chilled-water capacity ≥3,600,000 Btu/h
Simultaneous heating & cooling occurs above 60℉ outdoor air temperature
Required heat recovery system cooling capacity ≥7%total design chilled water capacity of acute inpatient hospital
|  |  | Indoor pool dehumidifier energy recovery | [6 empty] | Natatorium with heated indoor pool ≥500 sf shall include one of
Exhaust air sensible energy recovery ratio ≥50% or
Condenser heat recovery to use 100% of heat generated or
Exhaust air enthalpy recovery ratio ≥50%
Exhaust Systems
|  |  | Transfer air |  |  |  |  | Defined volume limits |  | Defined volume limits
|  |  | Kitchen exhaust systems | Replacement air directly into hood cavity ≤10% of hood airflow rate | Replacement air directly into hood cavity ≤10% of hood airflow rate | Replacement air directly into hood cavity ≤10% of hood airflow rate |  | Replacement air directly into hood cavity ≤10% of hood airflow rate |  | Replacement air directly into hood cavity ≤10% of hood airflow rate
|  |  |  | Conditioned supply air delivered to kitchen hood flow limitations | Conditioned supply air delivered to kitchen hood flow limitations | Conditioned supply air delivered to kitchen hood flow limitations |  | Conditioned supply air delivered to kitchen hood flow limitations |  | Conditioned supply air delivered to kitchen hood flow limitations
|  |  |  | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria |  | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria |  | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria
[8 empty] | Performance testing required |  | Performance testing required
|  |  | Fume (laboratory) hood systems that use exception for energy recovery | Variable exhaust & supply systems, or direct makeup supply for systems >defined cfm total exhaust | Variable exhaust & supply systems, or direct makeup supply for systems >defined cfm total exhaust |  |  | Variable exhaust & supply systems or heat recovery system for systems >5,000 cfm total exhaust |  | Variable exhaust & supply systems or heat recovery system for systems >5,000 cfm total exhaust
Radiant Heating Systems
|  |  | Unenclosed (outside building) spaces | Required and controlled by occupancy sensor or timer | Required and controlled by occupancy sensor or timer | Required and controlled by occupancy sensor or timer |  | Required with controls |  | Required with controls
|  |  | Enclosed Spaces |  |  |  |  | Conform with governing standards |  | Conform with governing standards
Hot Gas Bypass Limitation
Systems with Multiple Steps of Unloading (or Continuous Capacity Modulation in IECC)
|  |  | ≤240,000 Btu/h rated capacity | ≤50% maximum bypass capacity | ≤50% maximum bypass capacity | ≤50% maximum bypass capacity |  | ≤15% maximum bypass capacity |  | ≤15% maximum bypass capacity
|  |  | >240,000 Btu/h rated capacity | ≤25% maximum bypass capacity | ≤25% maximum bypass capacity | ≤25% maximum bypass capacity |  | ≤10% maximum bypass capacity |  | ≤10% maximum bypass capacity
Door Switches
|  |  | Any conditioned space with door, including doors with >50% glass, opening to outdoors |  |  |  |  | Doors provided with controls, that when door is open: |  | Doors provided with controls, that when door is open:
[8 empty] | Disable mechanical heating or reset heating setpoint to ≤55° within 5 minutes of door opening |  | Disable mechanical heating or reset heating setpoint to ≤55° within 5 minutes of door opening
[8 empty] | Disable mechanical cooling or reset cooling setpoint to ≥90° within 5 minutes of door opening. |  | Disable mechanical cooling or reset cooling setpoint to ≥90° within 5 minutes of door opening.
[8 empty] | Mechanical cooling may remain enabled if outdoor air temperature < space temperature |  | Mechanical cooling may remain enabled if outdoor air temperature < space temperature
[8 empty] | Exceptions: |  | Exceptions:
[8 empty] | Building entries with automatic closing devices |  | Building entries with automatic closing devices
[8 empty] | Space without thermostat |  | Space without thermostat
[8 empty] | Alterations to existing buildings |  | Alterations to existing buildings
[8 empty] | Loading docks |  | Loading docks
Refrigeration Equipment Performance
|  |  |  | Energy use limits (kWh per day) | Energy use limits (kWh per day) |  |  | Energy use limits (kWh per day)
Commercial refrigeration, holding temperature application
|  |  | Refrigerator with solid doors | 0.10 x V + 2.04 | 0.10 x V + 2.04 |  |  | 0.10 x V + 2.04
|  |  | Refrigerator with transparent doors | 0.12 x V + 3.34 | 0.12 x V + 3.34 |  |  | 0.12 x V + 3.34
|  |  | Freezers with solid doors | 0.40 x V + 1.38 | 0.40 x V + 1.38 |  |  | 0.40 x V + 1.38
|  |  | Freezers with transparent doors | 0.75 x V + 4.10 | 0.75 x V + 4.10 |  |  | 0.75 x V + 4.10
|  |  | Refrigerators/freezers with solid doors | Greater of 0.12 x V + 3.34 or 0.70 | Greater of 0.12 x V + 3.34 or 0.70 |  |  | Greater of 0.12 x V + 3.34 or 0.70
Commercial refrigeration, pulldown application
|  |  | Commercial refrigerators | 0.126 x V +3.51 | 0.126 x V + 3.51 |  |  | 0.126 x V + 3.51
Commercial refrigerators and freezers, remote condensing
|  |  | Vertical open, medium temp | 0.82 x TDA + 4.07 | 0.82 x TDA + 4.07 | 0.64 x TDA + 4.07 |  | 0.82 x TDA + 4.07 |  | 0.64 x TDA + 4.07
|  |  | Semivertical open, medium temp | 0.83 x TDA + 3.18 | 0.83 x TDA + 3.18 | 0.66 x TDA + 3.18 |  | 0.83 x TDA + 3.18 |  | 0.66 x TDA + 3.18
|  |  | Horizontal open, medium temp | 0.35 x TDA + 2.88 | 0.35 x TDA + 2.88 | 0.35 x TDA + 2.88 |  | 0.35 x TDA + 2.88 |  | 0.35 x TDA + 2.88
|  |  | Vertical open, low temp | 0.27 x TDA + 6.85 | 2.27 x TDA + 6.85 | 2.20 x TDA + 6.85 |  | 2.27 x TDA + 6.85 |  | 2.20 x TDA + 6.85
|  |  | Semiverticle open, low temp |  |  | 2.20 x TDA + 6.85 |  |  |  | 2.20 x TDA + 6.85
|  |  | Horizontal open, low temp | 0.57 x TDA + 6.88 | 0.57 x TDA + 6.88 | 0.55 x TDA + 6.88 |  | 0.57 x TDA + 6.88 |  | 0.55 x TDA + 6.88
|  |  | Vertical transparent door, medium temp | 0.22 x TDA + 1.95 | 0.22 x TDA + 1.95 | 0.15 x TDA + 1.95 |  | 0.22 x TDA + 1.95 |  | 0.15 x TDA + 1.95
|  |  | Vertical transparent door, low temp | 0.56 x TDA + 2.61 | 0.56 x TDA + 2.61 | 0.49 x TDA + 2.61 |  | 0.56 x TDA + 2.61 |  | 0.49 x TDA + 2.61
|  |  | Horizontal closed transparent, medium temp |  |  | 0.16 x TDA + 0.13 |  |  |  | 0.16 x TDA + 0.13
|  |  | Horizontal closed transparent, low temp |  |  | 0.34 x TDA + 0.26 |  |  |  | 0.34 x TDA + 0.26
|  |  | Vertical closed solid, medium temp |  |  | 0.10 x V + 0.26 |  |  |  | 0.10 x V + 0.26
|  |  | Vertical closed solid, low temp |  |  | 0.21 x V + 0.54 |  |  |  | 0.21 x V + 0.54
|  |  | Horizontal closed solid, medium temp |  |  | 0.10 x V + 0.26 |  |  |  | 0.10 x V + 0.26
|  |  | Horizontal closed solid, low temp |  |  | 0.21 x V + 0.54 |  |  |  | 0.21 x V + 0.54
|  |  | Service over counter, medium temp |  | 0.51 x TDA + 0.11 | 0.44 x TDA + 0.11 |  | 0.51 x TDA + 0.11 |  | 0.44 x TDA + 0.11
|  |  | Service over counter, low temp | 0.51 x TDA + 0.11 |  | 0.93 x TDA + 0.22 |  |  |  | 0.93 x TDA + 0.22
Commercial refrigerators and freezers, self-contained
|  |  | Vertical open, medium temp | 1.74 x TDA + 4.71 | 1.74 x TDA + 4.71 | 1.69 x TDA + 4.71 |  | 1.74 x TDA + 4.71 |  | 1.69 x TDA + 4.71
|  |  | Vertical open, low temp |  |  | 4.25 x TDA + 11.82 |  |  |  | 4.25 x TDA + 11.82
|  |  | Semivertical open, medium temp | 1.73 x TDA + 4.59 | 1.73 x TDA + 4.59 | 1.70 x TDA + 4.59 |  | 1.73 x TDA + 4.59 |  | 1.70 x TDA + 4.59
|  |  | Semivertical open, low temp |  |  | 4.26 x TDA + 11.51 |  |  |  | 4.26 x TDA + 11.51
|  |  | Horizontal open, medium temp | 0.77 x TDA + 5.55 | 0.77 x TDA + 5.55 | 0.72 x TDA + 5.55 |  | 0.77 x TDA + 5.55 |  | 0.72 x TDA + 5.55
|  |  | Horizontal open, low temp | 1.92 x TDA + 7.08 | 1.92 x TDA + 7.08 | 1.90 x TDA + 7.08 |  | 1.92 x TDA + 7.08 |  | 1.90 x TDA + 7.08
|  |  | Vertical closed transparent, medium temp |  |  | 0.10 x V + 0.86 |  |  |  | 0.10 x V + 0.86
|  |  | Vertical closed transparent, low temp |  |  | 0.29 x V +2.95 |  |  |  | 0.29 x V +2.95
|  |  | Vertical closed solid, medium temp |  |  | 0.05 x V + 1.36 |  |  |  | 0.05 x V + 1.36
|  |  | Vertical closed solid, low temp |  |  | 0.22 x V + 1.38 |  |  |  | 0.22 x V + 1.38
|  |  | Vertical transparent door, ice cream temp | 0.67 x TDA + 3.29 | 0.67 x TDA + 3.29 |  |  | 0.67 x TDA + 3.29
|  |  | Horizontal closed transparent, medium temp |  |  | 0.06 x V + 0.37 |  |  |  | 0.06 x V + 0.37
|  |  | Horizontal closed transparent, low temp |  |  | 0.08 x V + 1.23 |  |  |  | 0.08 x V + 1.23
|  |  | Horizontal closed solid, medium temp |  |  | 0.05 x V + 0.91 |  |  |  | 0.05 x V + 0.91
|  |  | Horizontal closed solid, low temp |  |  | 0.06 x V + 1.12 |  |  |  | 0.06 x V + 1.12
|  |  | Service over counter, medium temp |  |  | 0.52 x TDA + 1.00 |  |  |  | 0.52 x TDA + 1.00
|  |  | Service over counter, low temp |  |  | 1.10 x TDA + 2.10 |  |  |  | 1.10 x TDA + 2.10
|  |  | Vertical solid door, ice cream temp | 0.38 x V +0.88 | 0.38 x V +0.88 |  |  | 0.38 x V +0.88
|  |  | Horizontal transparent door, ice cream temp | 0.56 x TDA + 0.43 | 0.56 x TDA + 0.43 |  |  | 0.56 x TDA + 0.43
|  | Self-contained commercial refrigerators with transparent doors for pull-down temperature applications, medium temperature |  |  |  | 0.11 x V +0.81 |  |  |  | 0.11 x V +0.81
Commercial ice-cream freezers, remote condensing
|  |  | Vertical open |  |  | 2.79 x TDA + 8.7 |  |  |  | 2.79 x TDA + 8.7
|  |  | Semivertical open |  |  | 2.79 x TDA + 8.7 |  |  |  | 2.79 x TDA + 8.7
|  |  | Horizontal open |  |  | 0.70 x TDA + 8.74 |  |  |  | 0.70 x TDA + 8.74
|  |  | Vertical closed transparent |  |  | 0.58 x TDA + 3.05 |  |  |  | 0.58 x TDA + 3.05
|  |  | Horizontal closed transparent |  |  | 0.40 x TDA + 0.31 |  |  |  | 0.40 x TDA + 0.31
|  |  | Vertical closed solid |  |  | 0.25 x V + 0.63 |  |  |  | 0.25 x V + 0.63
|  |  | Horizontal closed solid |  |  | 0.25 x V + 0.63 |  |  |  | 0.25 x V + 0.63
|  |  | Service over counter |  |  | 1.09 x TDA + 0.26 |  |  |  | 1.09 x TDA + 0.26
Commercial ice-cream freezers, self contained
|  |  | Vertical open |  |  | 5.40 x TDA + 15.02 |  |  |  | 5.40 x TDA + 15.02
|  |  | Semivertical open |  |  | 5.41 x TDA + 14.63 |  |  |  | 5.41 x TDA + 14.63
|  |  | Horizontal open |  |  | 2.42 x TDA + 9.00 |  |  |  | 2.42 x TDA + 9.00
|  |  | Vertical closed transparent |  |  | 0.62 x TDA + 3.29 |  |  |  | 0.62 x TDA + 3.29
|  |  | Horizontal closed transparent |  |  | 0.56 x TDA + 0.43 |  |  |  | 0.56 x TDA + 0.43
|  |  | Vertical closed solid |  |  | 0.34 x V + 0.88 |  |  |  | 0.34 x V + 0.88
|  |  | Horizontal closed solid |  |  | 0.34 x V + 0.88 |  |  |  | 0.34 x V + 0.88
|  |  | Service over counter |  |  | 1.53 x TDA + 0.36 |  |  |  | 1.53 x TDA + 0.36
Commercial refrigerators and freezers, remote condensing
|  |  | Semivertical open, low temp | 2.27 x TDA + 6.85 | 2.27 x TDA + 6.85 |  |  | 2.27 x TDA + 6.85
|  |  | Vertical open, ice cream temp | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7 |  |  | 2.89 x TDA + 8.7
|  |  | Semivertical open, ice cream temp | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7 |  |  | 2.89 x TDA + 8.7
|  |  | Horizontal open, ice cream temp | 0.72 x TDA + 8.74 | 0.72 x TDA + 8.74 |  |  | 0.72 x TDA + 8.74
|  |  | Vertical transparent door, ice cream temp | 0.66 x TDA + 3.05 | 0.66 x TDA + 3.05 |  |  | 0.66 x TDA + 3.05
|  |  | Horizontal transparent door, medium temp | 0.16 x TDA + 0.13 | 0.16 x TDA + 0.13 |  |  | 0.16 x TDA + 0.13
|  |  | Horizontal transparent door, low temp | 0.34 x TDA + 0.26 | 0.34 x TDA + 0.26 |  |  | 0.34 x TDA + 0.26
|  |  | Horizontal transparent door, ice cream temp | 0.4 x TDA + 0.31 | 0.4 x TDA + 0.31 |  |  | 0.4 x TDA + 0.31
|  |  | Vertical solid door, medium temp | 0.11 x V + 0.26 | 0.11 x V + 0.26 |  |  | 0.11 x V + 0.26
|  |  | Vertical solid door, low temp | 0.23 x V + 0.54 | 0.23 x V + 0.54 |  |  | 0.23 x V + 0.54
|  |  | Vertical solid door, ice cream temp | 0.27 x V + 0.63 | 0.27 x V + 0.63 |  |  | 0.27 x V + 0.63
|  |  | Horizontal solid door, medium temp | 0.11 x V + 0.26 | 0.11 x V + 0.26 |  |  | 0.11 x V + 0.26
|  |  | Horizontal solid door, low temp | 0.23 x V + 0.54 | 0.23 x V + 0.54 |  |  | 0.23 x V + 0.54
|  |  | Horizontal solid door, ice cream temp | 0.27 x V + 0.63 | 0.27 x V + 0.63 |  |  | 0.27 x V + 0.63
|  |  | Service over counter, low temp | 1.08 x TDA + 0.22 | 1.08 x TDA + 0.22 |  |  | 1.08 x TDA + 0.22
|  |  | Service over counter, ice cream temp | 1.26 x TDA + 0.26 | 1.26 x TDA + 0.26 |  |  | 1.26 x TDA + 0.26
Commercial refrigerators and freezers, self-contained
|  |  | Vertical open, low temp | 4.37 x TDA + 11.82 | 4.37 x TDA + 11.82 |  |  | 4.37 x TDA + 11.82
|  |  | Vertical open, ice cream temp | 5.55 x TDA + 15.02 | 5.55 x TDA + 15.02 |  |  | 5.55 x TDA + 15.02
|  |  | Semivertical open, low temp | 4.34 x TDA + 11.51 | 4.34 x TDA + 11.51 |  |  | 4.34 x TDA + 11.51
|  |  | Semivertical open, ice cream temp | 5.52 x TDA + 14.63 | 5.52 x TDA + 14.63 |  |  | 5.52 x TDA + 14.63
|  |  | Horizontal open, ice cream temp | 2.44 x TDA + 9.0 | 2.44 x TDA + 9.0 |  |  | 2.44 x TDA + 9.0
|  |  | Service over counter, ice cream temp | 1.76 x TDA + 0.36 | 1.76 x TDA + 0.36 |  |  | 1.76 x TDA + 0.36
|  |  | Horizontal solid door, ice cream temp | 0.38 x V + 0.88 | 0.38 x V + 0.88 |  |  | 0.38 x V + 0.88
Walk-in Coolers & Walk-in Freezers that are NOT Either Site Assembled or Site Constructed
|  |  | Door-closers | Automatic within 1" of full closure | Automatic within 1" of full closure
|  |  | Doorway infiltration control | Strip door curtains, spring hinged doors or other method | Strip door curtains, spring hinged doors or other method
|  |  | Walk-in coolers & refrigerated warehouse coolers: wall, ceiling and door insulation | ≥R-25 | ≥R-25
|  |  | Walk-in freezers & refrigerated warehouse freezers: wall, ceiling and door insulation | ≥R-32 | ≥R-32
|  |  | Walk-in freezer floor insulation | ≥R-28 | ≥R-28
|  |  | Transparent reach-in doors for walk-in freezers & windows in walk-in freezer doors | Triple-pane glass, either filled with inert gas or heat-reflective treated glass | Triple-pane glass, either filled with inert gas or heat-reflective treated glass
|  |  | Windows & transparent reach-in doors for walk-in cooler doors | Double-pane or triple-pane, inert gas-filled, heat-reflective treated glass | Double-pane or triple-pane, inert gas-filled, heat-reflective treated glass
|  |  | Evaporative fan motors <1 hp and <460 v | Electronically commutated motors, brushless direct-current motors or 3-phase motors | Electronically commutated motors, brushless direct-current motors or 3-phase motors
|  |  | Condenser fan motors <1 hp | Electronically commutated motors, permanent split capacitor-type motors or 3- phase motors | Electronically commutated motors, permanent split capacitor-type motors or 3- phase motors
|  |  | Antisweat heaters without antisweat heater controls (total door rail, glass and frame heater power draw) | ≤7.1 W/sf of door opening for walk-in freezers | ≤7.1 W/sf of door opening for walk-in freezers
|  |  |  | ≤3.0 W/sf of door opening for walk-in coolers | ≤3.0 W/sf of door opening for walk-in coolers
|  |  | Antisweat heater control | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane
|  |  | Lights in walk-in coolers, walk-in freezers, and refrigerated warehouse freezers | Efficacy ≥40 lumens per watt, including ballast losses or | Efficacy ≥40 lumens per watt, including ballast losses or
|  |  |  | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy
Walk-in Coolers and Walk-in Freezers that are Site Assembled or Site Constructed
|  |  | Door-closers | Automatic within 1" of full closure | Automatic within 1" of full closure |  |  | Automatic within 1" of full closure |  | Automatic within 1" of full closure
|  |  | Doorway infiltration control | Strip door curtains, spring hinged doors or other method | Strip door curtains, spring hinged doors or other method |  |  | Strip door curtains, spring hinged doors or other method |  | Strip door curtains, spring hinged doors or other method
|  |  | Insulation | ≥R-25 for walls | ≥R-25 for walls |  |  | ≥R-25 for cooler walls |  | ≥R-25 for cooler walls
|  |  |  | ≥R-25 for ceiling | ≥R-25 for ceiling |  |  | ≥R-25 for cooler ceiling |  | ≥R-25 for cooler ceiling
|  |  |  | ≥R-25 for cooler doors | ≥R-32 for cooler doors |  |  | ≥R-25 for cooler doors |  | ≥R-25 for cooler doors
[8 empty] | ≥R-32 for freezer walls |  | ≥R-32 for freezer walls
[8 empty] | ≥R-32 for freezer ceiling |  | ≥R-32 for freezer ceiling
|  |  |  | ≥R-32 for freezer doors | ≥R-32 for freezer doors |  |  | ≥R-32 for freezer doors |  | ≥R-32 for freezer doors
|  |  |  | ≥R-28 for freezer floor | ≥R-28 for freezer floor |  |  | ≥R-28 for freezer floor |  | ≥R-28 for freezer floor
|  |  | Transparent reach-in doors for walk-in freezers & windows in opaque walk-in freezer doors | Triple-pane glass, either filled with inert gas or heat-reflective treated glass | Triple-pane glass, either filled with inert gas or heat-reflective treated glass |  |  | Triple-pane glass, either filled with inert gas or heat-reflective treated glass |  | Triple-pane glass, either filled with inert gas or heat-reflective treated glass or vacuum insulating glazing
|  |  | Transparent reach-in doors for walk-in coolers & windows in opaque doors for walk-in coolers | Double-pane, inert gas-filled, heat-reflective treated glass | Double-pane, inert gas-filled, heat-reflective treated glass |  |  | Double-pane, inert gas-filled, heat-reflective treated glass, or triple-pane glass with inert gas or heat-reflective treated glass |  | Double-pane, inert gas-filled, heat-reflective treated glass, or triple-pane glass with inert gas or heat-reflective treated glass or vacuum insulating glazing
|  |  | Evaporative fan motors <1 hp and <460 v | Electronically commutated motors or 3-phase motors | Electronically commutated motors or 3-phase motors |  |  | Electronically commutated motors (brushless direct-current motors) or 3-phase motors |  | Electronically commutated motors (brushless direct-current motors) or 3-phase motors
|  |  | Condenser fan motors <1 hp | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors |  |  | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors |  | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors
|  |  | Antisweat heaters without antisweat heater controls (total door rail, glass and frame heater power draw) | ≤7.1 W/sf of door opening for walk-in freezers | ≤7.1 W/sf of door opening for walk-in freezers |  |  | ≤7.1 W/sf of door opening for walk-in freezers |  | ≤7.1 W/sf of door opening for walk-in freezers
|  |  |  | ≤3.0 W/sf of door opening for walk-in coolers | ≤3.0 W/sf of door opening for walk-in coolers |  |  | ≤3.0 W/sf of door opening for walk-in coolers |  | ≤3.0 W/sf of door opening for walk-in coolers
|  |  | Antisweat heater control | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane |  |  | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane |  | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane
|  |  | Lights | Efficacy ≥40 lumens per watt, including ballast losses or | Efficacy ≥40 lumens per watt, including ballast losses or |  |  | Efficacy ≥40 lumens per watt, including ballast losses or |  | Efficacy ≥40 lumens per watt, including ballast losses or
|  |  |  | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy |  |  | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy |  | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy
|  |  | Walk-in freezer temperature based defrost termination control |  |  |  |  | First on upper temperature limit breach, second upon time limit breach |  | First on upper temperature limit breach, second upon time limit breach
Performance Standards, (Effective January 1, 2020)
|  | Walk-in cooler & freezer display door efficiency |  |  | Maximum energy consumption (kWh/day) | Maximum energy consumption (kWh/day) |  |  |  | Maximum energy consumption (kWh/day)
|  |  | Display door, medium temperature |  | 0.04 × Add + 0.41 | 0.04 × Add + 0.41 |  |  |  | 0.04 × Add + 0.41
|  |  | Display door, low temperature |  | 0.15 × Add + 0.29 | 0.15 × Add + 0.29 |  |  |  | 0.15 × Add + 0.29
|  | Walk-in cooler & freezer nondisplay door efficiency |  |  | Maximum energy consumption (kWh/day) | Maximum energy consumption (kWh/day) |  |  |  | Maximum energy consumption (kWh/day)
|  |  | Passage door, medium temperature |  | 0.05 × Add + 0.17 | 0.05 × And + 0.17 |  |  |  | 0.05 × And + 0.17
|  |  | Passage door, low temperature |  | 0.14 × Add + 4.8 | 0.14 × And + 4.8 |  |  |  | 0.14 × And + 4.8
|  |  | Freight door, medium temperature |  | 0.04 × Add + 1.9 | 0.04 × And + 1.9 |  |  |  | 0.04 × And + 1.9
|  |  | Freight door low temperature |  | 0.12 × Add + 5.6 | 0.12 × And + 5.6 |  |  |  | 0.12 × And + 5.6
|  | Walk-in cooler & freezer refrigeration system efficiency |  |  | Minimum annual walk-in energy factor AWEF (Btu/w-h) | Minimum annual walk-in energy factor AWEF (Btu/w-h) |  |  |  | Minimum annual walk-in energy factor AWEF (Btu/w-h)
|  |  | Dedicated condensing, medium temperature, indoor system |  | 5.61 | 5.61 |  |  |  | 5.61
|  |  | Dedicated condensing, medium temperature, outdoor system |  | 7.6 | 7.6 |  |  |  | 7.6
|  |  | Dedicated condensing, low temperature, indoor system, net capacity (qnet) <6,500 Btu/h |  |  | 9.091 x 10-5 x qnet + 1.81 |  |  |  | 9.091 x 10-5 x qnet + 1.81
|  |  | Dedicated condensing, low temperature, indoor system, net capacity (qnet) ≥6,500 Btu/h |  |  | 2.4 |  |  |  | 2.4
|  |  | Dedicated condensing, low temperature, outdoor system, net capacity (qnet) <6,500 Btu/h |  |  | 6.522 x 10-5 x qnet + 2.73 |  |  |  | 6.522 x 10-5 x qnet + 2.73
|  |  | Dedicated condensing, low temperature, outdoor system, net capacity (qnet) ≥6,500 Btu/h |  |  | 3.15 |  |  |  | 3.15
|  |  | Unit cooler, medium temperature |  |  | 9 |  |  |  | 9
|  |  | Unit cooler, low temperature, net capacity (qnet) <15,500 Btu/h |  |  | 1.575 x 10-5 x qnet + 3.91 |  |  |  | 1.575 x 10-5 x qnet + 3.91
|  |  | Unit cooler, low temperature, net capacity (qnet) ≥15,500 Btu/h |  |  | 4.15 |  |  |  | 4.15
|  |  | Dedicated condensing, medium temperature, indoor system >9,000 Btu/h capacity |  | 5.61
|  |  | Dedicated condensing, medium temperature, outdoor system >9,000 Btu/h capacity |  | 7.6
| Refrigerated Display Cases, Site Assembled or Site Constructed | [6 empty] | All Cases |  | All Cases
|  |  | Lighting control for display cases & glass doors on walk-in coolers & walk-in freezers | Time switch to turn lights off during nonbusiness hours or | Time switch to turn lights off during nonbusiness hours or |  |  | Time switch to turn lights off during nonbusiness hours with timed override or |  | Automatic time switch to turn lights off during nonbusiness hours with timed override or
|  |  |  | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated |  |  | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated |  | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated
|  |  | Low-temperature display cases | Temperature-based defrost termination control with time-limit default | Temperature-based defrost termination control with time-limit default |  |  | Temperature-based defrost termination control with time-limit default |  | Temperature-based defrost termination control with time-limit default
|  |  | Antisweat heater controls | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane |  |  | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane |  | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane
Refrigeration Systems
Refrigerated display cases, walk-in coolers or walk-in freezers served by remote compressors and remote condensers not located in a condensing unit (exception for working fluid that goes through both subcritical and super critical states or that uses ammonia refrigerant)
|  |  | Fan-powered condensers | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems
|  |  |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems
|  |  |  | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors |  | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors |  | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors
|  |  |  | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control |  | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control |  | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control
|  |  |  | Multiple fan condensers controlled in unison | Multiple fan condensers controlled in unison | Multiple fan condensers controlled in unison |  | Multiple fan condensers controlled in unison |  | Multiple fan condensers controlled in unison
|  |  |  | Minimum condensing temperature setpoint ≤70°F | Minimum condensing temperature setpoint ≤70°F | Minimum condensing temperature setpoint ≤70°F |  | Minimum condensing temperature setpoint ≤70°F |  | Minimum condensing temperature setpoint ≤70°F
|  |  | Compressor systems | Floating suction pressure control on compressors & multiple-compressor system suction groups | Floating suction pressure control on compressors & multiple-compressor system suction groups | Floating suction pressure control on compressors & multiple-compressor system suction groups |  | Floating suction pressure control on compressors & multiple-compressor system suction groups |  | Floating suction pressure control on compressors & multiple-compressor system suction groups
|  |  |  | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity |  | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity |  | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity
|  |  |  | Crankcase heaters cycled off during compressor operation | Crankcase heaters cycled off during compressor operation | Crankcase heaters cycled off during compressor operation |  | Crankcase heaters cycled off during compressor operation |  | Crankcase heaters cycled off during compressor operation
Service Water Heating
|  | Load Calculations | [5 empty] | Sizing systems and equipment in accordance with manufacturers' published guidelines or generally accepted engineering standards and handbooks |  | Sizing systems and equipment in accordance with manufacturers' published guidelines or generally accepted engineering standards and handbooks
|  | Water-heating equipment intended to be used to provide space heating |  | Allowed | Allowed | Allowed |  | Allowed with conditions |  | Allowed with conditions
|  |  |  | Meet minimum performance requirements for water-heating equipment | Meet minimum performance requirements for water-heating equipment | Meet minimum performance requirements for water-heating equipment |  | Allowed to provide space heating when one of following is met: |  | Allowed to provide space heating when one of following is met:
[8 empty] | ≤(13.3 × pmd 400)/𝑛, Btu/h standby loss |  | ≤(13.3 × pmd 400)/𝑛, Btu/h standby loss
[8 empty] | ahj agrees that single heat source will consume less energy than separate units |  | ahj agrees that single heat source will consume less energy than separate units
[8 empty] | <150,000 Btu/h energy input of combined boiler & water heater system |  | <150,000 Btu/h energy input of combined boiler & water heater system
Equipment Efficiency
High input-rated service water-heating-systems
|  |  |  | Gas-fired water heater in new building | Gas-fired water heater in new building | Gas-fired water heater in new building |  | Gas-fired water heater in new building |  | Gas-fired water heater in new building
|  |  | Singular piece serving entire building, rated ≥1,000,000 Btu/h | ≥90% Et | ≥90% Et | ≥92% Et |  | ≥90% Et |  | ≥90% Et
|  |  | Multiple pieces serving building, combined rated input ≥1,000,000 Btu/h | ≥90% Et, combined input-capacity-weighted-average | ≥90% Et, combined input-capacity-weighted-average | ≥90% Et, combined input-capacity-weighted-average |  | ≥90% Et, combined input-capacity-weighted-average |  | ≥90% Et, combined input-capacity-weighted-average
Electric table top water heaters
|  |  | ≤12 kW, <4,000 (Btu/H)/gal, ≥20 gal & ≤120 gal |  | 0.93 - 0.00132V, EF | 0.93 - 0.00132V, EF |  | per 10 CFR Part 430 |  | per 10 CFR Part 430
Electric storage water heaters
|  |  | ≤12 kW, <4,000 (Btu/H)/gal, ≥20 gal & ≤55 gal | 0.97 - 0.00132V, EF | 0.960 - 0.0003V, EF | 0.960 - 0.0003V, EF |  | per 10 CFR Part 430 |  | per 10 CFR Part 430
|  |  | ≤12 kW, <4,000 (Btu/H)/gal, ≥20 gal & ≤120 gal |  | 1.061 - 0.00168V, EF | 1.061 - 0.00168V, EF |  |  |  | per 10 CFR Part 430
|  |  | >12 kW, <4,000 (Btu/H)/gal | (0.3 + 27/Vm), %/h | (0.3 + 27/Vm), %/h | (0.3 + 27/Vm), %/h |  | 0.3 + 27/Vm %/h |  | SL ≤ 0.3 + 27/Vm %/h
|  |  | ≤24 amps and ≤250 volt, heat pump, (>55 gal & ≤120 gal) | 0.93 - 0.00132V, EF | 2.057 - 0.00113V, EF | 2.057 - 0.00113V, EF |  | per 10 CFR Part 430
Electric instantaneous water heaters
|  |  | ≤12 kW, <4,000 (Btu/H)/gal, <2 gal | [6 empty] | per 10 CFR Part 430
|  |  | >12 kW & ≤58.6 kW, ≥4,000 (Btu/h)/gal, ≤2 gal, ≤180℉ | [6 empty] | Very small DP | UEF = 0.80
[10 empty] | Low DP | UEF = 0.80
[10 empty] | Medium DP | UEF = 0.80
[10 empty] | High DP | UEF = 0.80
|  |  | ≤58.6 kW, ≥4,000 (Btu/h)/gal, ≤10 gal | [6 empty] | No requirement
|  |  | ≥58.6 kW, ≥4,000 (Btu/h)/gal, ≥10 gal | [6 empty] | No requirement
Gas storage water heaters
|  |  | ≤75,000 Btu/h, < 4,000 (Btu/h)/gal, ≥20 gal & ≤55 gal | 0.67 - 0.0019V, EF | 0.675 - 0.0015V, EF | 0.675 - 0.0015V, EF |  | per 10 CFR Part 430 |  | per 10 CFR Part 430
|  |  | ≤75,000 Btu/h, < 4,000 (Btu/h)/gal, >55 gal & ≤100 gal |  | 0.8012 - 0.00078V, EF | 0.8012 - 0.00078V, EF |  |  |  | per 10 CFR Part 430
|  |  | >75,000 Btu/h, < 4,000 (Btu/h)/gal |  |  |  |  | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
|  |  | >75,000 & ≤155,000 Btu/h, < 4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
|  |  | >75,000 & ≤105,000 Btu/h, ≥4,000 (Btu/h)/gal, ≤120 gal, ≤180℉ | [7 empty] | UEF
[10 empty] | Very small DP | 0.2674 - (0.0009 × Vr)
[10 empty] | Low DP | 0.5362 - (0.0012 × Vr)
[10 empty] | Medium DP | 0.6002 - (0.0011 × Vr)
[10 empty] | High DP | 0.6597 - (0.0009 × Vr)
|  |  | >105,000 Btu/h, <4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | [5 empty] | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
|  |  | >155,000 Btu/h, <4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et SL ≤ (Q/800 + 110√V), Btu/h | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
Gas instantaneous water heaters
|  |  | >50,000 & <200,000 Btu/h, ≥4,000 (Btu/h)/gal, <2 gal | 0.62 - 0.0019V, EF | 0.82 - 0.0019V, EF | 0.82 - 0.0019V, EF |  | per 10 CFR Part 430 |  | per 10 CFR Part 430
|  |  | ≥200,000 Btu/h, ≥4,000 (Btu/h)/gal <10 gal | 80% Et | 80% Et | 80% Et |  | 80% Et |  | 80% Et
|  |  | ≥200,000 Btu/h, ≥4,000 (Btu/h)/gal, ≥10 gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et SL ≤ (Q/800 + 110√V), Btu/h | 80% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 80% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
Oil storage water heaters
|  |  | ≤105,000 Btu/h, <4,000 (Btu/h)/gal, ≤50 gal) | 0.59 - 0.0019V, EF | 0.68 - 0.0019V, EF | 0.68 - 0.0019V, EF |  | per 10 CFR Part 430 |  | per 10 CFR Part 430
|  |  | >105,000 & ≤140,000 Btu/h, ≤4,000 (Btu/h)/gal, ≤120 gal, ≤180℉ | [7 empty] | UEF
[10 empty] | Very small DP | 0.2932 - (0.0015 × Vr)
[10 empty] | Low DP | 0.5596 - (0.0018 × Vr)
[10 empty] | Medium DP | 0.6194 - (0.0016 × Vr)
[10 empty] | High DP | 0.6740 - (0.0013 × Vr)
|  |  | >140,000 Btu/h, <4,000 (Btu/h)/gal | [6 empty] | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
|  |  | >105,000 Btu/h, <4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et SL ≤ (Q/800 + 110√V), Btu/h | 80% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
Oil instantaneous water heaters
|  |  | ≤210,000 Btu/h, ≥4,000 (Btu/h)/gal, <2 gal | 0.59 - 0.0019V, EF | 0.59 - 0.0019V, EF | 0.59 - 0.0019V, EF |  | per 10 CFR Part 430 |  | 80% Et EF ≥ 0.59 - 0.0005 × V
|  |  | >210,000 Btu/h, ≥4,000 (Btu/h)/gal, <10 gal | 80% Et | 80% Et | 80% Et |  | 80% Et |  | 80% Et
|  |  | >210,000 Btu/h, ≥4,000 (Btu/h)/gal, ≥10 gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 78% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 78% Et SL ≤ (Q/800 + 110√V), Btu/h
Hot water supply boilers, gas and oil
|  |  | ≥300,000 & <12,500,000 Btu/h, ≥4,000 (Btu/h)/gal, <10 gal | 80% Et | 80% Et | 80% Et |  | 80% Et |  | 80% Et
Hot water supply boilers, gas
|  |  | ≥300,000 & <12,500,000 Btu/h, ≥4,000 (Btu/h)/gal, ≥10 gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h |  |  | 80% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 80% Et SL ≤ (Q/800 + 110√V), Btu/h
Hot water supply boilers, oil
|  |  | >300,000 & <12,500,000 Btu/h ≥4,000 (Btu/h)/gal, ≥10 gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et SL ≤ (Q/800 + 110√V), Btu/h | 78% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 78% Et SL ≤ (Q/800 + 110√V), Btu/h |  | 78% Et SL ≤ (Q/800 + 110√V), Btu/h
|  | Pool heaters, gas |  | 82% Et | 82% Et | 82% Et |  | per 10 CFR Part 430 |  | per 10 CFR Part 430
|  | Heat pump pool heaters |  | 4.0 COP | 4.0 COP | 4.0 COP |  | 4.0 COP |  | 4.0 COP
|  | Unfired Storage Tanks |  | ≥R-12.5 | ≥R-12.5 | ≥R-12.5 |  | R-12.5 |  | R-12.5
Heat Traps
|  |  | Vertical risers serving storage water heaters and storage tanks serving noncirculating systems | Supplied internal heat traps or provided with heat traps on supply and discharge piping | Supplied internal heat traps or provided with heat traps on supply and discharge piping | Supplied internal heat traps or provided with heat traps on supply and discharge piping |  | Supplied internal heat traps or provided with heat traps on supply and discharge piping |  | Supplied internal heat traps or provided with heat traps on supply and discharge piping
Service Hot Water Piping Insulation
|  |  | Insulate | Inlet & outlet piping to heat trap or first 8 feet | Inlet & outlet piping to heat trap or first 8 feet | Inlet & outlet piping to heat trap or first 8 feet |  | Recirculating system piping |  | Recirculating system piping
|  |  |  | Piping that is heat traced | Piping that is heat traced | Piping that is heat traced |  | First 8' of outlet piping for constant temperature nonrecirculating storage system |  | First 8' of outlet piping for constant temperature nonrecirculating storage system
[8 empty] | First 8' of branch piping connecting to recirculating, heat trace-traced or impedance piping |  | First 8' of branch piping connecting to recirculating, heat trace-traced or impedance piping
[8 empty] | Inlet piping between storage tank and heat trap in nonrecirculating storage system |  | Inlet piping between storage tank and heat trap in nonrecirculating storage system
[8 empty] | Externally heated piping (heat trace or impedance heating) |  | Externally heated piping (heat trace or impedance heating)
|  |  | Minimum pipe insulation thickness | Use mechanical section requirements (Table C403.2.10) | Use mechanical section requirements (Table C403.11.3) | Use mechanical section requirements (Table C403.12.3) |  | Use mechanical section requirements (Table 6.8.3-1) |  | Use mechanical section requirements (Table 6.8.3-1)
Efficient Heated Water Supply Piping
|  |  | Heated water supply piping | Maximum flow rate | Maximum flow rate | Maximum flow rate
|  |  |  | 1/4", ≤0.5 gpm | 1/4", ≤0.5 gpm | 1/4", ≤0.5 gpm
|  |  |  | 5/16", ≤1 gpm | 5/16", ≤1 gpm | 5/16", ≤1 gpm
|  |  |  | 3/8", ≤1.5 gpm | 3/8", ≤1.5 gpm | 3/8", ≤1.5 gpm
Maximum allowable pipe length method
|  | Nominal pipe size to public lavatory faucets |  | Maximum piping length | Maximum piping length | Maximum piping length
|  |  | 1/4" | 6' | 6' | 6'
|  |  | 5/16" | 4' | 4' | 4'
|  |  | 3/8" | 3' | 3' | 3'
|  |  | 1/2" | 2' | 2' | 2'
|  |  | 5/8" | 1' | 1' | 1'
|  |  | 3/4" | 0.5' | 0.5' | 0.5'
|  |  | 7/8" | 0.5' | 0.5' | 0.5'
|  |  | 1" | 0.5' | 0.5' | 0.5'
|  |  | 1¼" | 0.5' | 0.5' | 0.5'
|  |  | 1½" | 0.5' | 0.5' | 0.5'
|  |  | ≥2" | 0.5' | 0.5' | 0.5'
|  | Nominal pipe size to other fixtures and appliances |  | Maximum piping length | Maximum piping length | Maximum piping length
|  |  | 1/4" | 50' | 50' | 50'
|  |  | 5/16" | 50' | 50' | 50'
|  |  | 3/8" | 50' | 50' | 50'
|  |  | 1/2" | 43' | 43' | 43'
|  |  | 5/8" | 32' | 32' | 32'
|  |  | 3/4" | 21' | 21' | 21'
|  |  | 7/8" | 16' | 16' | 16'
|  |  | 1" | 13' | 13' | 13'
|  |  | 1¼" | 8' | 8' | 8'
|  |  | 1½" | 6' | 6' | 6'
|  |  | ≥2" | 4' | 4' | 4'
Maximum allowable pipe volume method
|  |  | For public lavatory faucets | <2 ounces | <2 ounces | <2 ounces
|  |  | For other plumbing fixtures or plumbing appliances | <0.5 gallons | <0.5 gallons | <0.5 gallons
|  |  | Water volume determination | Internal volumes of pipe, fittings, valves, meters and manifolds between nearest source and termination of fixture supply piping using volumes below | Internal volumes of pipe, fittings, valves, meters and manifolds between nearest source and termination of fixture supply piping using volumes below | Internal volumes of pipe, fittings, valves, meters and manifolds between nearest source and termination of fixture supply piping using volumes below
|  | Nominal pipe size |  | Volume (liquid ounces per foot length) | Volume (liquid ounces per foot length) | Table C404.5.2.1
|  |  | 1/4" | 0.33 | 0.33 | Volume for nominal size of
|  |  | 5/16" | 0.5 | 0.5 | Type M Copper
|  |  | 3/8" | 0.75 | 0.75 | Type L Copper
|  |  | 1/2" | 1.5 | 1.5 | Type K Copper
|  |  | 5/8" | 2 | 2 | CPVC CTS SDR 11
|  |  | 3/4" | 3 | 3 | CPVC SCH 40
|  |  | 7/8" | 4 | 4 | CPVC SCH 80
|  |  | 1" | 5 | 5 | PE-TR SDR
|  |  | 1¼" | 8 | 8 | Composite ASTM F1281
|  |  | 1½" | 11 | 11 | PEX CTS SDR 9
|  |  | ≥2" | 18 | 18
Heated-water circulating and temperature maintenance systems
|  |  | Circulation systems | Provided with a circulation pump and return pipe or cold water supply pipe | Provide circulation pump and return pipe or cold water supply pipe | Provide circulation pump and return pipe or cold water supply pipe
|  |  |  | Automatically turns on pump when demand for hot water | Automatically turns on pump when demand for hot water | Automatically turns off pump when at desired temperature & no hot water demand
|  |  |  | Automatically turns off pump when at desired temperature & no hot water demand | Automatically turns off pump when at desired temperature & no hot water demand
|  |  | Electric heat trace systems | Automatically adjusts energy input to maintain desired water temperature in pipe during time heated water is used in the occupancy | Automatically adjusts energy input to maintain desired water temperature in pipe during time heated water is used in the occupancy | Automatically adjusts energy input to maintain desired water temperature in pipe during time heated water is used in the occupancy
|  |  |  | Automatically turns off when no hot water demand | Automatically turns off when no hot water demand | Automatically turns off when no hot water demand
|  |  | Controls for hot water storage | Pumping water between water heater and heated-water storage limited to <5 minutes after end of cycle | Pumping water between water heater and heated-water storage limited to <5 minutes after end of cycle | Pumping water between water heater and heated-water storage limited to <5 minutes after end of cycle
| Demand Recirculation Controls |  |  | Demand recirculation water system pumps from heated-water supply pipe back to heated-water source through cold-water supply pipe | Demand recirculation water system pumps from heated-water supply pipe back to heated-water source through cold-water supply pipe
|  |  | Required controls | Start pumping upon receiving signal from | Start pumping upon receiving signal from
|  |  |  | Action of a user | Action of a user
|  |  |  | Sensing the presence of a user | Sensing the presence of a user
|  |  |  | Sensing flow of water | Sensing flow of water
|  |  |  | Limit temperature of water entering cold-water piping to 104°F | Limit temperature of water entering cold-water piping to 104°F
Service Water Heating System Controls
|  |  | Storage temperature controls |  |  |  |  | Setpoint ≤120ºF or lower temperature compatible with intended use |  | Setpoint ≤120ºF or lower temperature compatible with intended use
|  |  | Temperature maintenance controls in hot water pipes |  |  |  |  | Automatic time switches/controls for extended periods when hot water not required |  | Automatic time switches/controls for extended periods when hot water not required
|  |  | Outlet temperature controls for lavatory faucets in public restrooms |  |  |  |  | Delivered ≤110ºF |  | Delivered ≤110ºF
|  |  | Circulating pump controls for storage tanks | Limit operation to 5 minutes after heating cycle | Limit operation to 5 minutes after heating cycle | Limit operation to 5 minutes after heating cycle |  | Limit operation to 5 minutes after heating cycle |  | Limit operation to 5 minutes after heating cycle
Drain Water Heat Recovery Units
|  |  |  | Comply with CSA B55.2 | Comply with CSA B55.2 | Comply with CSA B55.2
|  |  |  | Potable water-side pressure loss <10 psi at maximum design flow | Potable water-side pressure loss <10 psi at maximum design flow | Potable water-side pressure loss <10 psi at maximum design flow
|  |  |  | For Group R occupancies drain water heat recovery unit efficiency in accordance with CSA B55.1 | For Group R occupancies drain water heat recovery unit efficiency in accordance with CSA B55.1 | For Group R occupancies drain water heat recovery unit efficiency in accordance with CSA B55.1
Energy Consumption of Pools and In Ground Permanent Spas
Pool heaters
|  |  | Electric power to all heaters | Readily accessible on-off switch without adjusting setpoint | Readily accessible on-off switch without adjusting setpoint | Readily accessible on-off switch without adjusting setpoint |  | Readily accessible on-off switch without adjusting setpoint |  | Readily accessible on-off switch without adjusting setpoint
|  |  | Natural as-fired heaters | No continuously burning pilot | No continuously burning pilot | No continuously burning pilot |  | No continuously burning pilot |  | No continuously burning pilot
|  |  | Time switches | Installed on heaters and pumps | Installed on heaters and pumps | Installed on swimming pool heaters and pumps |  | Installed on swimming pool heaters and pumps |  | Installed on swimming pool heaters and pumps
Pool covers
|  |  |  | On outdoor heated pools & outdoor spas | On outdoor heated pools & outdoor spas | On outdoor heated pools & outdoor spas |  | On heated pools |  | On heated pools
|  |  | Water temperature ≤90ºF | Vapor retardant cover required | Vapor retardant cover required | Vapor retardant cover required |  | Vapor retardant cover required |  | Vapor retardant cover required
|  |  | Water temperature >90ºF | Vapor retardant cover required | Vapor retardant cover required | Vapor retardant cover required |  | Vapor retardant cover required with ≥R-12 insulation |  | Vapor retardant cover required with ≥R-12 insulation
Portable spas
|  |  | Control requirements | Meet APSP 14 | Meet APSP 14 | Meet APSP 14
Power
|  |  | Combined Feeder & Branch Circuit Voltage Drop |  | ≤5% Total | ≤5% Total |  | ≤5% Total |  | ≤5% Total
|  |  | Individual dwelling units | Separately metered in use group R-2 | Separately metered in use group R-2 | Separately metered in use group R-2
|  |  | Automatic receptacle control |  |  | ≥50% of all 125v 15- & 20-ampere receptacles in: |  | ≥50% of all 125v 15- & 20-ampere receptacles in: |  | ≥50% of all 125v 15- & 20-ampere receptacles in:
[6 empty] | Enclosed offices |  | Private offices |  | Private offices
[6 empty] | Conference rooms |  | Conference rooms |  | Conference rooms
[6 empty] | Rooms used primarily for printing and/or copying functions |  | Rooms used primarily for printing and/or copying functions |  | Rooms used primarily for printing and/or copying functions
[6 empty] | Break rooms |  | Break rooms |  | Break rooms
[6 empty] | Classrooms |  | Classrooms |  | Classrooms
[6 empty] | Individual workstations |  | Individual workstations |  | Individual workstations
[6 empty] | ≥25% branch circuit feeders installed for modular furniture not shown on construction documents |  | ≥25% branch circuit feeders installed for modular furniture not shown on construction documents |  | ≥25% branch circuit feeders installed for modular furniture not shown on construction documents
[6 empty] | Functions on: |  | Functions on: |  | Functions on:
[6 empty] | Scheduled basis or |  | Scheduled basis or |  | Scheduled basis or
[6 empty] | Occupant sensor or |  | Occupant sensor or |  | Occupant sensor or
[6 empty] | Signal from another control system |  | Signal from another control system |  | Signal from another control system
[6 empty] | Plug-in devices shall not comply |  |  |  | Plug-in devices shall not comply
Electrical energy monitoring
|  |  | Applicability |  |  | New buildings ≥25,000 sf |  | New buildings ≥25,000 sf |  | New buildings ≥25,000 sf
[6 empty] | Exceptions: |  | Exceptions: |  | Exceptions:
[6 empty] | R-2 occupancies & individual tenant spaces <5,000 sf with own utility services & meters |  | Individual tenant spaces <10,000 sf |  | Individual tenant spaces <10,000 sf
[8 empty] | Dwelling units |  | Dwelling units
[8 empty] | Residential buildings with <10,000 sf of common area |  | Residential buildings with <10,000 sf of common area
[8 empty] | Critical and equipment branches of NEC Article 517 |  | Critical and equipment branches of NEC Article 517
Receptacles specifically designated for equipment requiring continuous operation
Where controls would endanger safety or security
|  |  | Separately monitored area |  |  | Total building |  | Total building |  | Total building
[6 empty] | Each individual tenant space, excluding shared systems |  | Each individual tenant space, excluding shared systems |  | Each individual tenant space, excluding shared systems
|  |  | Separately monitored energy use |  |  | Total electrical energy |  | Total electrical energy |  | Total electrical energy
[6 empty] | Total HVAC systems |  | HVAC systems |  | HVAC systems
[6 empty] | Interior lighting |  | Interior lighting |  | Interior lighting
[6 empty] | Exterior lighting |  | Exterior lighting |  | Exterior lighting
[6 empty] | Receptacle circuits |  | Receptacle circuits |  | Receptacle circuits
Process load
Building operations & other miscellaneous loads
|  |  | Recording and reporting |  |  |  |  | Recorded minimum of every 15 minutes |  | Recorded minimum of every 15 minutes
[6 empty] | Reported at least hourly, daily, monthly and annually |  | Reported at least hourly, daily, monthly and annually |  | Reported at least hourly, daily, monthly and annually
[6 empty] | Store data for ≥36 months |  | Store data for ≥36 months |  | Store data for ≥36 months
Low Voltage Dry-Type Distribution Transformers
|  |  | Single phase (kVA) | Minimum efficiency | Minimum efficiency | Minimum efficiency |  | Minimum efficiency |  | Minimum efficiency
|  |  | 15 | 97.7% | 97.7% | 97.7% |  | 97.7% |  | 97.7%
|  |  | 25 | 98% | 98% | 98% |  | 98% |  | 98%
|  |  | 37.5 | 98.2% | 98.2% | 98.2% |  | 98.2% |  | 98.2%
|  |  | 50 | 98.3% | 98.3% | 98.3% |  | 98.3% |  | 98.3%
|  |  | 75 | 98.5% | 98.5% | 98.5% |  | 98.5% |  | 98.5%
|  |  | 100 | 98.6% | 98.6% | 98.6% |  | 98.6% |  | 98.6%
|  |  | 167 | 98.7% | 98.7% | 98.7% |  | 98.7% |  | 98.7%
|  |  | 250 | 98.8% | 98.8% | 98.8% |  | 98.8% |  | 98.8%
|  |  | 333 | 98.9% | 98.9% | 98.9% |  | 98.9% |  | 98.9%
|  |  | Three phase (kVA) | Minimum efficiency | Minimum efficiency | Minimum efficiency |  | Minimum efficiency |  | Minimum efficiency
|  |  | 15 | 97% | 97.89% | 97.89% |  | 97.89% |  | 97.89%
|  |  | 30 | 97.5% | 98.23% | 98.23% |  | 98.23% |  | 98.23%
|  |  | 45 | 97.7% | 98.4% | 98.4% |  | 98.4% |  | 98.4%
|  |  | 75 | 98% | 98.6% | 98.6% |  | 98.6% |  | 98.6%
|  |  | 112.5 | 98.2% | 98.74% | 98.74% |  | 98.74% |  | 98.74%
|  |  | 150 | 98.3% | 98.83% | 98.83% |  | 98.83% |  | 98.83%
|  |  | 225 | 98.5% | 98.94% | 98.94% |  | 98.94% |  | 98.94%
|  |  | 300 | 98.6% | 99.02% | 99.02% |  | 99.02% |  | 99.02%
|  |  | 500 | 98.7% | 99.14% | 99.14% |  | 99.14% |  | 99.14%
|  |  | 750 | 98.8% | 99.23% | 99.23% |  | 99.23% |  | 99.23%
|  |  | 1000 | 98.9% | 99.28% | 99.28% |  | 99.28% |  | 99.28%
|  | Computer Room Systems | [7 empty] | Distribution systems & equipment only serving computer room with ≥10 kW IT equipment shall comply with ASHRAE Standard 90.4, Energy Standard for Data Centers
Completion Requirements
|  |  | Record Drawings of Actual Installation |  |  | Construction documents to require submittal within 90 days of system acceptance |  | Construction documents to require submittal within 30 days of system acceptance |  | Construction documents to require submittal within 90 days of system acceptance
|  |  | Operating Manual |  |  | Construction documents to require submittal |  | Construction documents to require submittal |  | Construction documents to require submittal
|  |  | Maintenance Manual |  |  | Construction documents to require submittal |  | Construction documents to require submittal |  | Construction documents to require submittal
Lighting
Alterations
|  |  | Alterations requiring compliance with lighting power density | Replacement ≥50% of luminaires in a space or increased installed lighting power | Replacement ≥10% of luminaires or increases installed lighting power | Replacement ≥10% of luminaires or increases installed lighting power |  | Interior alterations involving >20% connected lighting load of space or area |  | Interior alterations involving >20% connected lighting load of space or area
|  |  |  | Replacement ≥10% of luminaires or increases installed lighting power |  |  |  | Interior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement |  | Interior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement
[8 empty] | Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power |  | Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power
[8 empty] | Exterior alterations involving connected lighting load |  | Exterior alterations involving connected lighting load
[8 empty] | Exterior alterations involving ≤20% connected lighting load of space or area need NOT comply but can not increase installed lighting power |  | Exterior alterations involving ≤20% connected lighting load of space or area need NOT comply but can not increase installed lighting power
[8 empty] | Exterior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement |  | Exterior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement
|  |  | Alterations requiring compliance with control requirements | Replacement ≥50% of luminaires in a space | Replacement ≥10% of luminaires or increases installed lighting power | Replacement ≥10% of luminaires or increases installed lighting power |  | Interior alterations involving >20% connected lighting load except for daylight responsive controls |  | Interior alterations involving >20% connected lighting load except for daylight responsive controls
[8 empty] | Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power |  | Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power
[8 empty] | Automatic/scheduled shutoff controls for interior lamp plus ballasts/drivers or one-for-one luminaire replacement |  | Automatic/scheduled shutoff controls for interior lamp plus ballasts/drivers or one-for-one luminaire replacement
[8 empty] | Automatic shutoff & power reduction controls for exterior alterations involving >20% connected lighting load of space or area |  | Automatic shutoff & power reduction controls for exterior alterations involving >20% connected lighting load of space or area
[8 empty] | Automatic/scheduled shutoff controls for exterior lamp plus ballasts/drivers or one-for-one luminaire replacement |  | Automatic/scheduled shutoff controls for exterior lamp plus ballasts/drivers or one-for-one luminaire replacement
| Luminaire Wattage | [6 empty] | Lighting power calculations for ballasts with adjustable ballast factors shall be based on the ballast factor that will be used in the space provided that the ballast factor is not user changeable. |  | Lighting power calculations for ballasts with adjustable ballast factors shall be based on the ballast factor that will be used in the space provided that the ballast factor is not user changeable.
| Lighting In Dwelling Units in Commercial Buildings |  |  | Exception when ≥75% lamps in permanently installed fixture are High-efficacy lamps or when ≥75% permanently installed interior fixtures fitted with high-efficiency lamps | ≥90% permanently installed interior fixtures contain only high-efficiency lamps or comply with Sections C405.2.4 & C405.3 | ≥90% permanently installed interior fixtures be provided by lamps ≥65 lm/W or luminaires ≥45 lm/W or comply with Sections C405.2.4 & C405.3 |  | Exception |  | ≥75% permanently installed interior fixtures contain only high-efficiency (≥55 lm/W) lamps or total luminaire efficacy ≥45 lm/W. No other provisions apply.
Lighting Controls
Interior Lighting Control
|  |  | Control device for each interior enclosed space (area) | Required controls vary with space type | Required controls vary by space type | Required controls vary by space type |  | All lighting control functions indicated in Table 9.6.1 for individual spaces |  | All lighting control functions indicated in Table 9.6.1 for individual spaces
[5 empty] | Luminaire level lighting controls (LLLC) vary by space type & independently capable of: | Luminaire level lighting controls (LLLC) vary by space type & independently capable of: |  | Functions labeled "REQ" are mandatory |  | Functions labeled "REQ" are mandatory
[8 empty] | 1) If space type labeled "ADD1", ≥1 of those functions shall be implemented in space |  | If space type labeled "ADD1", ≥1 of those functions shall be implemented in space
[5 empty] | Brightening or dimming lighting based on occupant activity | Brightening or dimming lighting based on occupant activity |  | 2) If space type labeled "ADD2", ≥1 of those functions shall be implemented in space |  | If space type labeled "ADD2", ≥1 of those functions shall be implemented in space
[5 empty] | Brightening or dimming artificial lighting to maintain desired light level | Brightening or dimming artificial lighting to maintain desired light level |  | Functions: |  | Functions:
[8 empty] | Local control: ≥1 manual lighting controls in the space |  | Local control: ≥1 manual lighting controls in the space
[8 empty] | Restricted to manual ON |  | Restricted to manual ON
[5 empty] | Modifying performance parameters to account for control strategy changes, configurations & reconfigurations | Modifying performance parameters to account for control strategy changes, configurations & reconfigurations |  | Restricted to partial automatic ON |  | Restricted to partial automatic ON
[8 empty] | Bilevel lighting control |  | Bilevel lighting control
[8 empty] | Automatic daylight responsive controls for sidelighting |  | Automatic daylight responsive controls for sidelighting
[8 empty] | Automatic daylight responsive controls for toplighting |  | Automatic daylight responsive controls for toplighting
[8 empty] | Automatic partial OFF (full OFF complies) |  | Automatic partial OFF (full OFF complies)
[8 empty] | Automatic full OFF |  | Automatic full OFF
[8 empty] | Scheduled shutoff |  | Scheduled shutoff
Scheduled OFF during nonbusiness hours
|  |  | Time-switch control (Automatic interior lighting shutoff controls for all spaces) | Each area not provided with occupant sensor controls | Each area not provided with occupant sensor controls | Each area not provided with occupant sensor controls |  | All lighting (except emergency lighting that is automatically off during normal operation) automatically off during scheduled unoccupied periods |  | All lighting (except emergency lighting that is automatically off during normal operation) automatically off during scheduled unoccupied periods
|  |  |  | Provided with manual control | Provided with manual control | Control functions |  | Local control (spaces ≤2,500 sf if space ≤10,000 sf and ≤10,000 sf otherwise) |  | Local control (spaces ≤2,500 sf if space ≤10,000 sf and ≤10,000 sf otherwise)
|  |  |  | Control functions | Control functions | Automatically turn off lights when scheduled to be unoccupied |  | Scheduled OFF |  | Scheduled OFF
|  |  |  | ≥7-day clock | ≥7-day clock | ≥7-day clock |  | Controlled by: |  | Controlled by:
|  |  |  | 7 different day types per week | 7 different day types per week | 7 different day types per week |  | Time-of-day device |  | Time-of-day device
|  |  |  | Incorporate automatic holiday feature | Incorporate automatic holiday feature | Incorporate automatic holiday feature |  | Signal from another automatic control or alarm/security system |  | Signal from another automatic control or alarm/security system
|  |  |  | >10 hour program backup capability | >10 hour program backup capability | >10 hour program backup capability
|  |  |  | ≤2 hour manual override | ≤2 hour manual override | ≤2 hour manual override
|  |  |  | Individual override switch controls area ≤5,000 sq. ft. | Individual override switch controls area ≤5,000 sq. ft. | Individual override switch controls area ≤5,000 sq. ft.
|  |  | Occupancy sensor space control | Occupancy sensor controls required in: | Occupant sensor controls required in: | Occupant sensor controls required in: |  | In space types per Table 9.6.1 |  | In space types per Table 9.6.1
|  |  |  | Classrooms / lecture / training rooms | Classrooms / lecture / training rooms | Classrooms / lecture / training rooms
|  |  |  | Conference / meeting/ multipurpose rooms | Conference / meeting / multipurpose rooms | Conference / meeting / multipurpose rooms
|  |  |  | Copy / print rooms | Copy / print rooms | Copy / print rooms
|  |  |  | Lounges | Lounges / breakrooms | Lounges / breakrooms
|  |  |  | Employee lunch & break rooms | Enclosed offices | Enclosed offices
|  |  |  | Private offices | Open plan office areas | Open plan office areas
|  |  |  | Restrooms | Restrooms | Restrooms
|  |  |  | Storage rooms | Storage rooms | Storage rooms
|  |  |  | Janitorial closets |  | Corridors
|  |  |  | Locker rooms | Locker rooms | Locker rooms
|  |  |  | Other spaces ≤300 sq. ft. enclosed by floor-to-ceiling height partitions | Other spaces ≤300 sq. ft. enclosed by floor-to-ceiling height partitions | Other spaces ≤300 sq. ft. enclosed by floor-to-ceiling height partitions
|  |  |  | Warehouses | Warehouse storage areas | Warehouse storage areas
|  |  | Occupant sensor control function | Occupancy sensors shall be: | Occupant sensors shall be: | Occupant sensors shall be: |  | Per Table 9.6.1 |  | Per Table 9.6.1
|  |  |  | Automatic off within 30 minutes; | Automatic off within 20 minutes; | Automatic off within 20 minutes; |  | Restricted to manual ON |  | Restricted to manual ON
|  |  |  | Manual on or automatic on to ≤50% power; | Manual on or automatic on to ≤50% power; | Manual on or automatic on to ≤50% power; |  | Restricted to partial ON: ≤50% automatically turn on and remainder to be manually turned on |  | Restricted to partial ON: ≤50% automatically turn on and remainder to be manually turned on
|  |  |  | Manual off control to allow occupants to turn off lights | Manual off control to allow occupants to turn off lights | Manual off control to allow occupants to turn off lights
[8 empty] | Automatic partial OFF (full OFF complies): automatically reduces lighting by ≥50% within 20 minutes of occupants leaving |  | Automatic partial OFF (full OFF complies): automatically reduces lighting by ≥50% within 20 minutes of occupants leaving
[8 empty] | Automatic full OFF within 20 minutes of occupants leaving |  | Automatic full OFF within 20 minutes of occupants leaving
|  |  | Occupant sensor control function in warehouses | Automatically reduce lighting power ≥50% in isleways and open areas | Automatically reduce lighting power ≥50% in isleways and open areas | Automatically reduce lighting power ≤50% in controlled area within 20 minutes
|  |  |  | Independently control lighting in each isleway | Independently control lighting in each isleway | Independently control lighting in each isleway
|  |  |  | Not control lighting beyond isleway being controlled | Not control lighting beyond isleway being controlled | Lights not turned off by occupant sensors shall be turned off by time-switch
Manual off control to allow occupants to turn off lights
|  |  | Occupant sensor control function in open plan office area |  | Configured so general lighting control zones ≤600 sf of open office | Configured so general lighting control zones ≤600 sf of open office
[5 empty] | Automatically turn off general lighting within 20 minutes after all occupants left open office space | Automatically turn on general lighting in control zone upon occupancy & be permitted to turn general lighting in unoccupied zones ≤20% full power
[5 empty] | Automatically reduce general lighting ≥80% in control zone within 20 minutes of all occupants leaving zone | Automatically turn off general lighting in all control zones within 20 minutes after all occupants left open office space
[5 empty] | Daylight responsive control activate space general lighting or control zone general lighting when occupancy detected | General lighting in control zone turned off or uniformly reduced ≤20% full power after all occupants left control zone
|  |  | Occupant sensor control function in corridors |  |  | Uniformly reduce lighting power ≤50% within 20 minutes of occupants leaving space
|  |  | Light-reduction controls | Manual control capable to reduce connected load ≤50% in reasonably uniform pattern | Manual control capable to reduce connected load ≤50% in reasonably uniform pattern | When not provided with occupant sensor, manual control capable to reduce connected load ≥50% in reasonably uniform pattern with intermediate step between 30% and 70% or with continuous dimming control |  | Bilevel lighting control: Step between full ON and full OFF to be between 30% & 70% of full lighting power |  | Bilevel lighting control: Step between full ON and full OFF to be between 30% & 70% of full lighting power
|  |  | Manual controls | Readily accessible and located where the controlled lights are | Readily accessible and located where the controlled lights are | Readily accessible and located where the controlled lights are |  | Readily accessible and located where the controlled lights are |  | Readily accessible and located where the controlled lights are
|  |  | Daylight responsive controls | Control lighting in spaces with >150 watts of general lighting within sidelight daylight zone | Control lighting in spaces with >150 watts of general lighting within sidelit zone | Control lighting in spaces with >150 watts of general lighting within primary sidelit zone or with 300 watts of general lighting within sidelit daylight zones |  | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within primary sidelight daylight zone |  | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within primary sidelight daylight zone
|  |  |  | Control lighting in spaces with >150 watts of general lighting within toplight daylight zone | Control lighting in spaces with >150 watts of general lighting within toplit zone | Control lighting in spaces with >150 watts of general lighting within toplit zone |  | Photocontrol lighting in spaces with ≥300 watts of general lighting completely or partially within primary and secondary sidelight daylight zone |  | Photocontrol lighting in spaces with ≥300 watts of general lighting completely or partially within primary and secondary sidelight daylight zone
|  |  |  | Exceptions: | Exceptions: | Exceptions: |  | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within daylight areas under skylights & roof monitors |  | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within daylight areas under skylights & roof monitors
|  |  |  | 1) Direct patient care space in health care facility | 1) Direct patient care space in health care facility | 1) Direct patient care space in health care facility
|  |  |  | 2) Dwelling & sleeping units | 2) Lighting require to have specific application control | 2) Sidelit zones on first floor above grade in Group A-2 and Group M occupancies
|  |  |  | 3) Lighting require to have specific application control | 3) Sidelit zones on first floor above grade in Group A-2 and Group M occupancies | 3) New buildings where total connected lighting powered ≤ adjusted interior lighting power allowance calculated per Equation 4-9
|  |  |  | 4) Sidelight daylight zones on first floor above grade in Group A-2 and Group M occupancies | 4) New buildings where total connected lighting powered ≤ adjusted interior lighting power allowance calculated per Equation 4-9
|  |  | Daylight-responsive control functions (Daylight zone control) | Lights in toplight daylight zones controlled independently of lights in sidelight daylight zones | Lights in toplit zones controlled independently of lights in sidelit zones | Lights in toplit zones controlled independently of lights in sidelit zones |  | General lighting in secondary sidelighted area controlled independently of primary sidelight area |  | General lighting in secondary sidelighted area controlled independently of primary sidelight area
Lights in primary sidelit zone controlled independently of lights in secondary sidelit zone
|  |  |  | Configured to be calibrated from within that space by authorized personnel | Configured to be calibrated from within that space by authorized personnel | Configured to be calibrated from within that space by authorized personnel |  | General lighting in overlapping toplighted and sidelighted daylight areas controlled together |  | General lighting in overlapping toplighted and sidelighted daylight areas controlled together
|  |  |  | Readily accessible calibration mechanism | Readily accessible calibration mechanism | Readily accessible calibration mechanism |  | Readily accessible calibration mechanism |  | Readily accessible calibration mechanism
|  |  |  | Continuous dimming controls from full light output to ≤15% of full light output in offices, classrooms, laboratories and library reading rooms | Continuous dimming controls from full light output to ≤15% of full light output in offices, classrooms, laboratories and library reading rooms | Continuous dimming controls from full light output to ≤15% of full light output |  | Photocontrol to reduce lighting by continuous dimming or with one control point between 50% & 70%, with second control point between 20% & 40% (or lowest dimming level the technology allows) and third control point is OFF |  | Photocontrol to reduce lighting by continuous dimming ≤20%
|  |  |  | Capable of complete shutoff of all controlled lights | Capable of complete shutoff of all controlled lights | Capable of complete shutoff of all controlled lights |  | Capable of complete shutoff of all controlled lights |  | Capable of complete shutoff of all controlled lights
|  |  |  | Independent control of lights in sidelight daylight zones facing different cardinal orientations | Independent control of lights in sidelit zones facing different cardinal orientations | Independent control of lights in sidelit zones facing different cardinal orientations
[6 empty] | When occupant sensor controls have reduced power to an unoccupied setpoint, daylight responsive controls shall continue to adjust light levels but not increase above unoccupied setpoint |  |  |  | When occupant sensor controls have reduced power to an unoccupied setpoint, daylight responsive controls shall continue to adjust light levels but not increase above unoccupied setpoint
|  |  | Sidelight daylight zone | Floor area next to vertical fenestration | Floor area adjacent to vertical fenestration | Floor area adjacent to vertical fenestration |  | Primary sidelight area |  | Primary sidelight area
|  |  |  | Where fenestration located in a wall, | Where fenestration located in a wall, | Where fenestration located in a wall, |  | Directly adjacent to vertical fenestration |  | Directly adjacent to vertical fenestration
|  |  |  | Extends laterally to nearest full-height wall, or up to 1.0 times height from floor to top of fenestration | Extends laterally to nearest full-height wall, or up to 1.0 times height from floor to top of fenestration | Extends laterally to nearest full-height wall, or up to 1.0 times height from floor to top of fenestration |  | Width is width of fenestration plus, on each side, the smaller of: |  | Width is width of fenestration plus, on each side, the smaller of:
[8 empty] | 1) ½ fenestration head height (floor to top of glazing) or |  | 1) ½ fenestration head height (floor to top of glazing) or
|  |  |  | Extends longitudinally from edge of fenestration to nearest full-height wall, or 2 feet, whichever is less | Extends longitudinally from edge of fenestration to nearest full-height wall, or 2 feet, whichever is less | Extends longitudinally from edge of fenestration to nearest full-height wall, or 0.5 times (2 feet?), whichever is less |  | 2) Distance to opaque vertical obstruction ≥5' high |  | 2) Distance to opaque vertical obstruction ≥5' high
[8 empty] | Depth is smaller of perpendicular distance from fenestration: |  | Depth is smaller of perpendicular distance from fenestration:
[8 empty] | 1) Vertical head height or |  | 1) Vertical head height or
|  |  |  | Area of fenestration ≥ 24 sq. ft. | Area of fenestration ≥ 24 sq. ft. |  |  | 2) Distance to opaque vertical obstruction ≥5' high |  | 2) Distance to opaque vertical obstruction ≥5' high
|  |  |  | Distance from fenestration to any building or geological formation which would block access to daylight is greater than height from bottom of fenestration to top of building or geological formation | Distance from fenestration to any building or geological formation which would block access to daylight is greater than height from bottom of fenestration to top of building or geological formation | Where fenestration located in a rooftop monitor, |  | Secondary sidelight area |  | Secondary sidelight area
[8 empty] | Directly adjacent to primary sidelight area |  | Directly adjacent to primary sidelight area
[6 empty] | Extends laterally to nearest obstruction that is taller than 0.7 times ceiling height, or up to 1.0 times height from floor to bottom of fenestration, whichever is less |  | Width is width of fenestration plus, on each side, the smaller of: |  | Width is width of fenestration plus, on each side, the smaller of:
[8 empty] | 1) ½ fenestration head height (floor to top of glazing) or |  | 1) ½ fenestration head height (floor to top of glazing) or
[6 empty] | Extends longitudinally from edge of fenestration to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.25 times height from floor to bottom of fenestration, whichever is less |  | 2) Distance to opaque vertical obstruction ≥5' high |  | 2) Distance to opaque vertical obstruction ≥5' high
[8 empty] | Depth is smaller of perpendicular distance from fenestration: |  | Depth is smaller of perpendicular distance from fenestration:
|  |  |  | Where located in existing building, visible transmittance of fenestration ≥0.2 | Where located in existing building, visible transmittance of fenestration ≥0.2 |  |  | 1) Vertical head height or |  | 1) Vertical head height or
[6 empty] | Secondary sidelit daylight zone |  | 2) Distance to opaque vertical obstruction ≥5' high |  | 2) Distance to opaque vertical obstruction ≥5' high
[6 empty] | Directly adjacent to primary sidelit zone |  | Secondary sidelight area |  | Secondary sidelight area
[6 empty] | Extends laterlly to 2.0 times height from floor to top of fenestration or to nearest full height wall, whichever is less |  | If primary sidelight area ends at opaque vertical obstruction ≥5' high, there is no secondary sidelight area |  | If primary sidelight area ends at opaque vertical obstruction ≥5' high, there is no secondary sidelight area
|  |  |  | Where fenestration located in a rooftop monitor, |  | Extends longitudinally from edge of fenestration to nearest full height wall or 2 feet, whichever is less |  | Daylight area under roof monitor |  | Daylight area under roof monitor
|  |  |  | Extends laterally to nearest obstruction that is taller than 0.7 times ceiling height, or up to 1.0 times height from floor to bottom of fenestration, whichever is less |  |  |  | Width is width of fenestration plus, on each side, the smaller of: |  | Width is width of fenestration plus, on each side, the smaller of:
[6 empty] | Area of fenestration ≥ 24 sq. ft. |  | 1) 2 ft or |  | 1) 2 ft or
[6 empty] | Distance from fenestration to any building or geological formation which would block access to daylight is greater than one half height from bottom of fenestration to top of building or geological formation |  | 2) Distance to opaque vertical obstruction ≥5' high or |  | 2) Distance to opaque vertical obstruction ≥5' high or
|  |  |  | Extends longitudinally from edge of fenestration to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.25 times height from floor to bottom of fenestration, whichever is less |  |  |  | 3) Distance to edge of any primary sidelighted area |  | 3) Distance to edge of any primary sidelighted area
[8 empty] | Depth is smaller inward distance from bottom edge of fenestration: |  | Depth is smaller inward distance from bottom edge of fenestration:
[6 empty] | Visible transmittance of fenestration ≥0.20 |  | 1) Monitor sill height (floor to bottom edge of glazing) or |  | 1) Monitor sill height (floor to bottom edge of glazing) or
[6 empty] | Projection factor shading fenestration ≤1.0 for orientations ≤45º from true north or ≤1.5 for all other orientations |  | 2) Distance to nearest opaque vertical obstruction, where any part of obstruction is farther than the difference between height of obstruction and monitor sill height |  | 2) Distance to nearest opaque vertical obstruction, where any part of obstruction is farther than the difference between height of obstruction and monitor sill height
|  |  | Toplight daylight zone | Floor area underneath roof fenestration assembly | Floor area underneath roof fenestration assembly | Floor area underneath roof fenestration assembly |  | Daylight area under skylight |  | Daylight area under skylight
|  |  |  | Extends laterally and longitudinally beyond edge of roof fenestration assembly to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.7 times ceiling height, whichever is less | Extends laterally and longitudinally beyond edge of roof fenestration assembly to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.7 times ceiling height, whichever is less | Extends laterally and longitudinally beyond edge of roof fenestration assembly to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.7 times ceiling height, whichever is less |  | Area bounded by opening beneath skylight & horizontally in each direction, smaller of: |  | Area bounded by opening beneath skylight & horizontally in each direction, smaller of:
[8 empty] | a) 70% ceiling height or |  | a) 70% ceiling height or
[6 empty] | No building or geological formation blocks direct sunlight from hitting assembly at peak solar angle on summer solstice |  | b) Distance to nearest opaque vertical obstruction where any part of obstruction is father than 70% distance between top of obstruction & ceiling at lowest edge of skylight |  | b) Distance to nearest opaque vertical obstruction where any part of obstruction is father than 70% distance between top of obstruction & ceiling at lowest edge of skylight
[5 empty] | Where fenestration located in a rooftop monitor, | Product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylit zone ≥0.008 |  | Product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylit zone ≥0.006 |  | Product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylit zone ≥0.006
Extends laterally to nearest obstruction that is taller than 0.7 times ceiling height, or up to 1.0 times height from floor to bottom of fenestration, whichever is less
Extends longitudinally from edge of fenestration to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.25 times height from floor to bottom of fenestration, whichever is less
|  |  |  | No building or geological formation blocks direct sunlight from hitting assembly at peak solar angle on summer solstice | No building or geological formation blocks direct sunlight from hitting assembly at peak solar angle on summer solstice
|  |  |  | Where located in existing building, the product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylight zone ≥0.008 | Product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylit zone ≥0.008
|  |  | Atriums |  |  | Daylit zones established at top floor surrounding the atrium and at floor of atrium space & not on intermediate floors |  |  |  | Daylit zones established at top floor surrounding the atrium and at floor of atrium space & not on intermediate floors
Specific application controls
|  |  | Luminaires for which additional lighting power is claimed |  |  | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting |  | Wattage only exempt if in addition to general lighting & is independently controlled |  | Wattage only exempt if in addition to general lighting & is independently controlled
|  |  | Display/accent lighting | Dedicated control independent of controls for other lighting within room or space | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting |  | Separate control device |  | Separate control device
|  |  | Case lighting | Dedicated control independent of controls for other lighting within room or space | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting |  | Separate control device |  | Separate control device
|  |  | Hotel, motel sleeping units and guest suites | Master control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room | Control device or system capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room | Control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room |  | Control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room |  | Control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room
[8 empty] | Separate occupant sensing control for bathrooms, turn off ≤30 minutes after occupants left bathroom |  | Separate occupant sensing control for bathrooms, turn off ≤30 minutes after occupants left bathroom
|  |  | Supplemental task lighting | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power) | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting |  | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power) |  | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power)
|  |  | Permanently installed luminaires in dwelling units |  | Occupant sensor or light reduction controls | Occupant sensor or light reduction controls |  | Other than lamp efficacy, no other provisions of Section 9 apply |  | Other than lamp efficacy, no other provisions of Section 9 apply
|  |  | Nonvisual lighting | Dedicated control independent of controls for other lighting within room or space | Time-switch control independent of controls for other lighting within room or space | Time-switch control independent of controls for other lighting within room or space |  | Separate control device |  | Separate control device
|  |  | Demonstration lighting | Dedicated control independent of controls for other lighting within room or space | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting |  | Separate control device |  | Separate control device
|  |  | Parking Garage Lighting Control |  |  | Automatic lighting shutoff |  | Automatic lighting shutoff |  | Automatic lighting shutoff
[6 empty] | Automatic ≥30% reduction when no activity ≤20 minutes |  | Automatic ≥30% reduction when no activity ≤20 minutes |  | Automatic ≥50% reduction when no activity ≤20 minutes
[6 empty] | Automatic reduction of transition zone lighting to ≤50% from sunset to sunrise |  | ≥50% automatic reduction from sunset to sunrise on covered vehicle entrance & exit ramps |  | Automatic reduction of transition zone lighting to ≤night time general lighting level from sunset to sunrise
[6 empty] | Automatic reduction ≥50% in response to daylight within 20 feet of perimeter wall openings |  | Photocontrol dimming within 20' of wall with ≥40% window wall ratio & no exterior obstructions |  | Photocontrol dimming within 20 feet of perimeter wall opening ≥24 sf
|  | Exterior lighting controls |  | Automatic shut-off when sufficient daylight available | Automatic shut-off when sufficient daylight available | Automatic shut-off when sufficient daylight available |  | Automatic shut-off when sufficient daylight available |  | Automatic shut-off when sufficient daylight available
|  |  |  | Facade or landscape lighting automatically shuts as function of dusk/dawn and set opening and closing time | Facade & landscape lighting automatically shuts off set 1 hour after business closing to ≤1 hour before business opening | Facade & landscape lighting automatically shuts off set 1 hour after business closing to ≤1 hour before business opening |  | Facade and landscape lighting automatically off between midnight or business closing and 6 am or business opening |  | Facade and landscape lighting automatically off between midnight or business closing and 6 am or business opening
|  |  |  | Other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes | Other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to ≥6 am, from ≤1 hour after business closing to ≥1 hour before business opening or during any period when activity not detected for >15 minutes | Other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥50% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes |  | Signage & other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes |  | Signage & other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥50% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes
[6 empty] | Automatically reduce power ≥50% to each parking area luminaires >78 W and ≤24 ft mounting height when no activity detected in illuminated area for ≤15 minutes. ≤1,500 W controlled together |  | Automatically reduce power ≥50% to each parking area luminaires >78 W and ≤24 ft mounting height when no activity detected in illuminated area for ≤15 minutes |  | Automatically reduce power ≥50% to each parking area luminaires >78 W and ≤24 ft mounting height when no activity detected in illuminated area for ≤15 minutes. ≤1,500 W controlled together
| Functional Testing |  |  | In commissioning section | In commissioning section | In commissioning section |  |  |  | In section
| Exit Signs |  |  | ≤5 watts per side for internally illuminated
Interior Lighting Power
|  | Building Area Method - Lighting Power Densities |  | Standard Section C405
|  |  |  | w/sf | w/sf | w/sf |  | w/sf |  | w/sf
|  |  | Automotive Facility | 0.8 | 0.71 | 0.75 |  | 0.71 |  | 0.75
|  |  | Convention Center | 1.01 | 0.76 | 0.64 |  | 0.76 |  | 0.64
|  |  | Courthouse | 1.01 | 0.9 | 0.79 |  | 0.9 |  | 0.79
|  |  | Dining: Bar Lounge/Leisure | 1.01 | 0.9 | 0.8 |  | 0.9 |  | 0.8
|  |  | Dining: Cafeteria/Fast Food | 0.9 | 0.79 | 0.76 |  | 0.79 |  | 0.76
|  |  | Dining: Family | 0.95 | 0.78 | 0.71 |  | 0.78 |  | 0.71
|  |  | Dormitory | 0.57 | 0.61 | 0.53 |  | 0.61 |  | 0.53
|  |  | Exercise Center | 0.84 | 0.65 | 0.72 |  | 0.65 |  | 0.72
|  |  | Fire Station | 0.67 | 0.53 | 0.56 |  | 0.53 |  | 0.56
|  |  | Gymnasium | 0.94 | 0.68 | 0.76 |  | 0.68 |  | 0.76
|  |  | Healthcare - Clinic | 0.9 | 0.82 | 0.81 |  | 0.82 |  | 0.81
|  |  | Hospital | 1.05 | 1.05 | 0.96 |  | 1.05 |  | 0.96
|  |  | Hotel | 0.87 | 0.75 | 0.56 |  | 0.75 |  | 0.56
|  |  | Library | 1.19 | 0.78 | 0.83 |  | 0.78 |  | 0.83
|  |  | Manufacturing Facility | 1.17 | 0.9 | 0.82 |  | 0.9 |  | 0.82
|  |  | Motel | 0.87 | 0.75 | 0.56 |  | 0.75 |  | 0.56
|  |  | Motion Picture Theater | 0.76 | 0.83 | 0.44 |  | 0.83 |  | 0.44
|  |  | Multi-Family | 0.51 | 0.68 | 0.45 |  | 0.68 |  | 0.45
|  |  | Museum | 1.02 | 1.06 | 0.55 |  | 1.06 |  | 0.55
|  |  | Office | 0.82 | 0.79 | 0.64 |  | 0.79 |  | 0.64
|  |  | Parking Garage | 0.21 | 0.15 | 0.18 |  | 0.15 |  | 0.18
|  |  | Penitentiary | 0.81 | 0.75 | 0.69 |  | 0.75 |  | 0.69
|  |  | Performing Arts Theater | 1.39 | 1.18 | 0.84 |  | 1.18 |  | 0.84
|  |  | Police Station | 0.87 | 0.8 | 0.66 |  | 0.8 |  | 0.66
|  |  | Post Office | 0.87 | 0.67 | 0.65 |  | 0.67 |  | 0.65
|  |  | Religious Building | 1 | 0.94 | 0.67 |  | 0.94 |  | 0.67
|  |  | Retail | 1.26 | 1.06 | 0.84 |  | 1.06 |  | 0.84
|  |  | School/University | 0.87 | 0.81 | 0.72 |  | 0.81 |  | 0.72
|  |  | Sports Arena | 0.91 | 0.87 | 0.76 |  | 0.87 |  | 0.76
|  |  | Town Hall | 0.89 | 0.8 | 0.69 |  | 0.8 |  | 0.69
|  |  | Transportation | 0.7 | 0.61 | 0.5 |  | 0.61 |  | 0.5
|  |  | Warehouse | 0.66 | 0.48 | 0.45 |  | 0.48 |  | 0.45
|  |  | Workshop | 1.19 | 0.9 | 0.91 |  | 0.9 |  | 0.91
Space-by-Space Method, Common Space Types - Lighting Power Densities
|  | (Space with Multiple Functions Shall Be Broken up Into Smaller Subspaces) |  | Standard Section C405 |  | w/sf |  | w/sf | RCR Threshold | w/sf | RCR Threshold
Atrium - First 40' in height
|  |  | Atrium <40' in height | 0.03 per ft (total height) | 0.03 per ft (total height) | 0.48
|  |  | Atrium <20' in height |  |  |  |  | 0.03 | N/A | 0.39 | NA
|  |  | Atrium ≥20' and ≤40' |  |  |  |  | 0.03 | N/A | 0.48 | NA
|  |  | Atrium >40' in height | 0.40 + 0.02 per foot in total height | 0.40 + 0.02 per foot in total height | 0.6 |  | 0.40 + 0.02 per foot in total height | N/A | 0.6 | NA
|  |  | Audience seating area in auditorium | 0.63 | 0.63 | 0.61 |  | 0.63 | 6 | 0.61 | 6
|  |  | Audience seating area in convention center | 0.82 | 0.82 |  |  | 0.82 | 4
|  |  | Audience seating area in gymnasium | 0.65 | 0.65 | 0.23 |  | 0.65 | 6 | 0.23 | 6
|  |  | Audience seating area in performing arts theatre | 2.43 | 2.03 | 1.16 |  | 2.03 | 8 | 1.16 | 8
|  |  | Audience seating area in motion picture theatre | 1.14 | 1.14 | 0.27 |  | 1.14 | 4 | 0.27 | 4
|  |  | Audience seating area in penitentiary | 0.28 | 0.28 | 0.67 |  | 0.28 | 4 | 0.67 | 4
|  |  | Audience seating area in religious building | 1.53 | 1.53 | 0.72 |  | 1.53 | 4 | 0.72 | 4
|  |  | Audience seating area in sports arena | 0.43 | 0.43 | 0.33 |  | 0.43 | 4 | 0.33 | 4
|  |  | Audience seating area in other | 0.43 | 0.43 | 0.33 |  | 0.43 | 4 | 0.23 | 4
|  |  | Banking activity area | 1.01 | 0.86 | 0.61 |  | 0.86 | 6 | 0.61 | 6
|  |  | Classroom / lecture hall / training room in penitentiary | 1.34 | 1.34 | 0.89 |  | 1.34 | 4 | 0.89 | 4
|  |  | Classroom / lecture hall / training room in other | 1.24 | 0.96 | 0.71 |  | 0.92 | 4 | 0.71 | 4
|  |  | Conference / meeting / multipurpose room | 1.23 | 1.07 | 0.97 |  | 1.07 | 6 | 0.97 | 6
|  |  | Confinement cells |  |  |  |  | 0.81 | 6 | 0.7 | 6
|  |  | Copy / print room | 0.72 | 0.56 | 0.31 |  | 0.56 | 6 | 0.31 | 6
|  | Corridor in facility for visually impaired (and not used primarily by staff) |  | 0.92 | 0.92 | 0.71 |  | 0.92 | Width <8' | 0.71 | Width <8'
|  |  | Corridor in hospital | 0.79 | 0.92 | 0.71 |  | 0.92 | Width <8' | 0.71 | Width <8'
|  |  | Corridor in manufacturing facility | 0.41 | 0.29 |  |  | 0.29 | Width <8'
|  |  | Corridor in other | 0.66 | 0.66 | 0.71 |  | 0.66 | Width <8' | 0.41 | Width <8'
|  |  | Courtroom | 1.72 | 1.39 | 1.2 |  | 1.39 | 6 | 1.2 | 6
|  |  | Computer room | 1.71 | 1.33 | 0.94 |  | 1.33 | 4 | 0.94 | 4
|  |  | Dining area in penitentiary | 0.96 | 0.96 | 0.42 |  | 0.96 | 6 | 0.42 | 6
|  | Dining area in facility for visually impaired (and not used primarily by staff) |  | 1.9 | 2 | 1.27 |  | 2 | 4 | 1.27 | 4
|  |  | Dining area in bar/lounge or leisure Dining | 1.07 | 0.93 | 0.86 |  | 0.93 | 4 | 0.86 | 4
|  |  | Dining area in cafeteria or fast food dining | 0.65 | 0.63 | 0.4 |  | 0.63 | 4 | 0.4 | 4
|  |  | Dining area in family dining | 0.89 | 0.71 | 0.6 |  | 0.71 | 4 | 0.6 | 4
|  |  | Dining area in other | 0.65 | 0.63 | 0.43 |  | 0.63 | 4 | 0.43 | 4
|  |  | Electrical / mechanical room | 0.95 | 0.43 | 0.43 |  | 0.43 | 6 | 0.43 | 6
|  |  | Emergency vehicle garage | 0.56 | 0.41 | 0.52 |  | 0.41 | 4 | 0.52 | 4
|  |  | Food preparation area | 1.21 | 1.06 | 1.09 |  | 1.06 | 6 | 1.09 | 6
|  |  | Guest room | 0.47 | 0.77 | 0.41 |  | 0.77 | 6 | 0.41 | 6
|  |  | Laboratory in or as classroom | 1.43 | 1.2 | 1.11 |  | 1.2 | 6 | 1.11 | 6
|  |  | Laboratory, otherwise | 1.81 | 1.45 | 1.33 |  | 1.45 | 6 | 1.33 | 6
|  |  | Laundry / washing area | 0.6 | 0.43 | 0.53 |  | 0.43 | 4 | 0.53 | 4
|  |  | Loading dock, interior | 0.47 | 0.58 | 0.88 |  | 0.58 | 6 | 0.88 | 6
|  | Lobby in facility for visually impaired (and not used primarily by staff) |  | 1.8 | 2.03 | 1.69 |  | 2.03 | 4 | 1.69 | 4
|  |  | Lobby for elevator | 0.64 | 0.68 | 0.65 |  | 0.69 | 6 | 0.65 | 6
|  |  | Lobby in hotel | 1.06 | 1.06 | 0.51 |  | 1.06 | 4 | 0.51 | 4
|  |  | Lobby in performing arts theater | 2 | 1.7 | 1.25 |  | 1.7 | 6 | 1.25 | 6
|  |  | Lobby in motion picture theater | 0.59 | 0.45 | 0.23 |  | 0.45 | 4 | 0.23 | 4
|  |  | Lobby, otherwise | 0.9 | 1 | 0.84 |  | 1 | 4 | 0.84 | 4
|  |  | Locker Room | 0.75 | 0.48 | 0.52 |  | 0.48 | 6 | 0.52 | 6
|  |  | Lounge / breakroom in healthcare facility | 0.92 | 0.78 | 0.42 |  | 0.78 | 6 | 0.42 | 6
|  |  | Lounge / breakroom, otherwise | 0.73 | 0.62 | 0.59 |  | 0.62 | 4 | 0.59 | 4
|  |  | Office - enclosed | 1.11 | 0.93 | 0.74 |  | 0.93 (≤250 sf) | 8 | 0.74 (≤250 sf) | 8
[8 empty] | 0.93 (>250 sf) | 8 | 0.66 (>250 sf) | 8
|  |  | Office - open plan | 0.98 | 0.81 | 0.61 |  | 0.81 | 4 | 0.61 | 4
|  |  | Parking area, interior | 0.19 | 0.14 | 0.15 |  | 0.14 | 4 | 0.15 | 4
|  |  | Pharmacy area | 1.68 | 1.34 | 1.66 |  | 1.34 | 6 | 1.66 | 6
|  | Restroom in facility for visually impaired (and not used primarily by staff) |  | 1.21 | 0.96 | 1.26 |  | 0.96 | 8 | 1.26 | 8
|  |  | Restroom, otherwise | 0.98 | 0.85 | 0.63 |  | 0.85 | 8 | 0.63 | 8
|  |  | Sales Area (for Accent Lighting see Additional Interior Lighting | 1.59 | 1.22 | 1.05 |  | 1.22 | 6 | 1.05 | 6
|  |  | Seating area, general | 0.54 | 0.42 | 0.23 |  | 0.42 | 4 | 0.23 | 4
|  |  | Stairway |  |  |  |  | Use space LPD containing stairway |  | Use space LPD containing stairway
|  |  | Stairwell | 0.69 | 0.58 | 0.49 |  | 0.58 | 10 | 0.49 | 10
|  |  | Storage room | 0.63 | 0.46 | 0.38 |  | 0.46 | 6
|  |  | Storage room <50 sf |  |  |  |  | 0.97 | 6 | 0.51 | 9
|  |  | Storage room ≥50 sf |  |  |  |  | 0.46 | 6 | 0.38 | 6
|  |  | Vehicular maintenance area | 0.67 | 0.56 | 0.6 |  | 0.56 | 4 | 0.6 | 4
|  |  | Workshop | 1.59 | 1.14 | 1.26 |  | 1.14 | 6 | 1.26 | 6
|  | Space-by-Space Method, Building-Specific Space Types - Lighting Power Densities |  | Standard Section C405 |  |  |  | w/sf | RCR Threshold | w/sf | RCR Threshold
Facility for visually impaired
|  |  | Chapel (and not used primarily by staff) | 2.21 | 1.06 | 0.7 |  | 1.06 | 4 | 0.7 | 4
|  |  | Recreation room / common living room(and not used primarily by staff) | 2.41 | 1.8 | 1.77 |  | 1.8 | 6 | 1.77 | 6
|  |  | Convention center exhibit space | 1.45 | 0.88 | 0.61 |  | 0.88 | 4 | 0.61 | 4
|  |  | Dormitory - Living Quarters | 0.38 | 0.54 | 0.5 |  | 0.54 | 8 | 0.5 | 8
|  |  | Fire station sleeping quarters | 0.22 | 0.2 | 0.23 |  | 0.2 | 6 | 0.23 | 6
Gymnasium / fitness center
|  |  | Exercise area | 0.72 | 0.5 | 0.9 |  | 0.5 | 4 | 0.9 | 4
|  |  | Playing Area | 1.2 | 0.82 | 0.85 |  | 0.82 | 4 | 0.85 | 4
Healthcare facility
|  |  | Exam/Treatment | 1.66 | 1.68 | 1.4 |  | 1.68 | 8 | 1.4 | 8
|  |  | Medical Supply | 0.74 | 0.54 | 0.62 |  | 0.54 | 6 | 0.62 | 6
|  |  | Nursery | 0.88 | 1 | 0.92 |  | 1 | 6 | 0.92 | 6
|  |  | Nurses' Station | 0.71 | 0.81 | 1.17 |  | 0.81 | 6 | 1.17 | 6
|  |  | Operating Room | 2.48 | 2.17 | 2.26 |  | 2.17 | 6 | 2.26 | 6
|  |  | Patient Room | 0.62 | 0.62 | 0.68 |  | 0.62 | 6 | 0.68 | 6
|  |  | Physical Therapy | 0.91 | 0.84 | 0.91 |  | 0.84 | 6 | 0.91 | 6
|  |  | Radiology / Imaging | 1.51 | 1.06 | 0.94 |  | 1.06 | 6 | 0.94 | 6
|  |  | Recovery | 1.15 | 1.03 | 1.25 |  | 1.03 | 6 | 1.25 | 6
Library
|  |  | Reading area | 1.06 | 0.82 | 0.96 |  | 0.82 | 4 | 0.96 | 4
|  |  | Stacks | 1.71 | 1.2 | 1.18 |  | 1.2 | 4 | 1.18 | 4
Manufacturing
Corridor / transition
|  |  | Detailed manufacturing | 1.29 | 0.93 | 0.8 |  | 0.93 | 4 | 0.8 | 4
|  |  | Equipment room | 0.74 | 0.65 | 0.76 |  | 0.65 | 6 | 0.76 | 6
|  |  | Extra high bay (>50' ceiling height) | 1.05 | 1.05 | 1.42 |  | 1.05 | 4 | 1.42 | 8
|  |  | High bay (25' - 50' ceiling height) | 1.23 | 0.75 | 1.24 |  | 0.75 | 4 | 1.24 | 6
|  |  | Low bay (<25' ceiling height) | 1.19 | 0.96 | 0.86 |  | 0.96 | 4 | 0.86 | 3
Museum
|  |  | General exhibition | 1.05 | 1.05 | 0.31 |  | 1.05 | 6 | 0.31 | 6
|  |  | restoration | 1.02 | 0.85 | 1.1 |  | 0.85 | 6 | 1.1 | 6
|  |  | Performing art theater - dressing room | 0.61 | 0.36 | 0.41 |  | 0.36 | 6 | 0.41 | 6
|  |  | Post office - sorting area | 0.94 | 0.68 | 0.76 |  | 0.68 | 4 | 0.76 | 4
Religious buildings
|  |  | Fellowship hall | 0.64 | 0.55 | 0.54 |  | 0.55 | 4 | 0.54 | 4
|  |  | Worship, pulpit, choir | 1.53 | 1.53 | 0.85 |  | 1.53 | 4 | 0.85 | 4
Retail
|  |  | Dressing / fitting room | 0.71 | 0.5 | 0.51 |  | 0.5 | 8 | 0.51 | 8
|  |  | Mall concourse | 1.1 | 0.9 | 0.82 |  | 0.9 | 4 | 0.82 | 4
Sales area (for accent lighting see additional interior lighting)
Sports arena - playing area
|  |  | Class 4 facility | 1.2 | 1.13 | 0.86 |  | 1.13 | 4 | 0.86 | 4
|  |  | Class 3 facility | 1.8 | 1.7 | 1.3 |  | 1.7 | 4 | 1.3 | 4
|  |  | Class 2 facility | 2.4 | 1.96 | 2.01 |  | 1.96 | 4 | 2.01 | 4
|  |  | Class 1 facility | 3.68 | 2.47 | 2.94 |  | 2.47 | 4 | 2.94 | 4
Transportation facility
|  |  | Baggage / carousel area | 0.53 | 0.45 | 0.39 |  | 0.45 | 4 | 0.39 | 4
|  |  | Airport - concourse | 0.36 | 0.31 | 0.25 |  | 0.31 | 4 | 0.25 | 4
|  |  | Terminal - ticket counter | 0.8 | 0.62 | 0.51 |  | 0.62 | 4 | 0.51 | 4
Warehouse storage area
|  |  | Medium to bulky, palletized items | 0.58 | 0.35 | 0.33 |  | 0.35 | 4 | 0.33 | 4
|  |  | Smaller, hand-carried items | 0.95 | 0.69 | 0.69 |  | 0.69 | 6 | 0.69 | 6
|  |  | Room Geometry Adjustment when using space-by-space method |  |  |  |  | Allowed for individual spaces where empty room RCR is >threshold, LPD increase = base space LPD x 0.20 |  | Allowed for individual spaces where empty room RCR is >threshold, LPD increase = base space LPD x 0.20
|  |  | Additional interior lighting power when using space-by-space method for specific lighting functions | For specified luminaires and not used for any other purpose | For specified luminaires and not used for any other purpose | For specified luminaires and not used for any other purpose |  | For specified lighting function and not for any other purpose |  | For specified lighting function and not for any other purpose
|  |  |  | Controlled separately from general lighting | Automatically controlled separately from general lighting | Automatically controlled separately from general lighting |  | Automatically controlled separately from general lighting |  | Controlled separately from general lighting
|  |  |  | Turn off during nonbusiness hours | Turn off during nonbusiness hours |  |  | Turn off during nonbusiness hours |  | Turn off during nonbusiness hours
|  |  |  | ≤1.0 w/sf of such space for decorative appearance or for highlighting art or exhibits | ≤0.9 w/sf in lobbies & ≤0.75 w/sf in other spaces for decorative appearance or for highlighting art or exhibits | ≤0.9 w/sf in lobbies & ≤0.75 w/sf in other spaces for decorative appearance or for highlighting art or exhibits |  | ≤0.75 w/sf of space for decorative appearance or for highlighting art or exhibits |  | ≤0.75 w/sf of space for decorative appearance or for highlighting art or exhibits
|  |  |  | In sales area to highlight merchandise, Additional ILPA = 500 w + (Retail Area 1 x 0.6 w/sf) + (Retail Area 2 x 0.6 w/sf) + (Retail Area 3 x 1.4 w/sf) + (Retail Area 4 x 2.5 w/sf) | In sales area to highlight merchandise, Additional ILPA = 1000 w + (Retail Area 1 x 0.45 w/sf) + (Retail Area 2 x 0.45 w/sf) + (Retail Area 3 x 1.05 w/sf) + (Retail Area 4 x 1.87 w/sf) | In sales area to highlight merchandise, Additional ILPA = 1000 w + (Retail Area 1 x 0.45 w/sf) + (Retail Area 2 x 0.45 w/sf) + (Retail Area 3 x 1.05 w/sf) + (Retail Area 4 x 1.87 w/sf) |  | In sales area to highlight merchandise, Additional ILPA = 1000 w + (Retail Area 1 x 0.45 w/sf) + (Retail Area 2 x 0.45 w/sf) + (Retail Area 3 x 1.05 w/sf) + (Retail Area 4 x 1.88 w/sf) |  | In sales area to highlight merchandise, Additional ILPA = 1000 w + (Retail Area 1 x 0.45 w/sf) + (Retail Area 2 x 0.45 w/sf) + (Retail Area 3 x 1.05 w/sf) + (Retail Area 4 x 1.88 w/sf)
|  | Additional Interior Lighting Power using non-mandatory controls | [5 empty] | Allowed when using space-by-space method and when all mandatory controls are used |  | Allowed when using space-by-space method and when all mandatory controls are used
[8 empty] | * Limited to workstation-specific luminaires |  | * Limited to workstation-specific luminaires
[8 empty] | ** Occupant allowed to select preferred light level |  | ** Occupant allowed to select preferred light level
*** Cannot be used to satisfy exemption
[8 empty] | Control Factors |  | Control Factors
Manual, continuous dimming controls or programmable multi-level dimming control
|  |  | Open office |  |  |  |  | 0.05 |  | 0.05
|  |  | Private office |  |  |  |  | 0.05 |  | 0.05
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  |  |  | 0.1 |  | 0.1
|  |  | Retail sales area |  |  |  |  | 0.1 |  | 0.1
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  |  |  | 0 |  | 0
Programmable multi-level dimming control using programmable time scheduling
|  |  | Open office |  |  |  |  | 0.05 |  | 0.05
|  |  | Private office |  |  |  |  | 0.05 |  | 0.05
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  |  |  | 0.1 |  | 0.1
|  |  | Retail sales area |  |  |  |  | 0.1 |  | 0.1
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  |  |  | 0.1 |  | 0.1
Occupancy sensors controlling downlight component of workstation specific luminaires with continuous dimming to OFF capabilities
|  |  | Open office |  |  |  |  | 0.25* |  | 0.25*
|  |  | Private office |  |  |  |  | 0 |  | 0
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  |  |  | 0 |  | 0
|  |  | Retail sales area |  |  |  |  | 0 |  | 0
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  |  |  | 0 |  | 0
Occupancy sensors controlling downlight component of workstation specific luminaires with continuous dimming to OFF capabilities in combination with personal continuous dimming control of downlight illumination by workstation occupant
|  |  | Open office |  |  |  |  | 0.30* ** |  | 0.30* **
|  |  | Private office |  |  |  |  | 0 |  | 0
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  |  |  | 0 |  | 0
|  |  | Retail sales area |  |  |  |  | 0 |  | 0
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  |  |  | 0 |  | 0
Automatic continuous daylight dimming in secondary sidelighted areas
|  |  | Open office |  |  |  |  | 0.10***
|  |  | Private office |  |  |  |  | 0.10***
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  |  |  | 0.10***
|  |  | Retail sales area |  |  |  |  | 0.10***
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  |  |  | 0.10***
Exterior Lighting
Lighting Power Limits for Building Exteriors
Zone 0: undeveloped area within national parks, state parks, forest land, rural areas and other undeveloped areas defined by authority having jurisdiction
|  | Zone 0: Tradable surfaces | [5 empty] | No allowance |  | No allowance
Zone 0: Nontradable surfaces
|  |  | Roadway/parking entry, trail head, & toilet facility, or other locations approved by authority having jurisdiction |  |  |  |  | Single luminaire ≤25 w |  | Single luminaire ≤25 w
Zone 1: developed areas of national parks, state parks, forest land and rural areas
Zone 1: Tradable surfaces
|  |  | Base site allowance | 500 w | 350 w | 350 w |  | 350 w |  | 350 w
|  |  | Uncovered parking areas and drives | 0.04 w/sf | 0.03 w/sf | 0.03 w/sf |  | 0.03 w/sf |  | 0.03 w/sf
|  |  | Walkways <10 ft wide | 0.7 w/lin ft | 0.5 w/lin ft | 0.5 w/lin ft |  | 0.5 w/lin ft |  | 0.5 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.14 w/sf | 0.10 w/sf | 0.10 w/sf |  | 0.10 w/sf |  | 0.10 w/sf
|  |  | Dining areas |  | 0.65 w/sf | 0.65 w/sf |  | 0.65 w/sf |  | 0.65 w/sf
|  |  | Stairways | 0.75 w/sf | 0.60 w/sf | 0.60 w/sf |  | 0.60 w/sf |  | 0.60 w/sf
|  |  | Pedestrian tunnels | 0.15 w/sf | 0.12 w/sf | 0.12 w/sf |  | 0.12 w/sf |  | 0.12 w/sf
|  |  | Landscaping |  | 0.03 w/sf | 0.03 w/sf |  | 0.03 w/sf |  | 0.03 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 20 w/lin ft of Door Width | 14 w/lin ft of opening | 14 w/lin ft of opening |  | 14 w/lin ft of opening |  | 14 w/lin ft of opening
|  |  | Entry canopies | 0.25 w/sf | 0.20 w/sf | 0.20 w/sf |  | 0.20 w/sf |  | 0.20 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 0.60 w/sf | 0.40 w/sf | 0.40 w/sf |  | 0.40 w/sf |  | 0.40 w/sf
|  |  | Outdoor open sales areas | 0.25 w/sf | 0.2 w/sf | 0.2 w/sf |  | 0.2 w/sf |  | 0.2 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | No Allowance | No Allowance | No Allowance |  | No Allowance |  | No Allowance
|  | Zone 1: Non-tradable surfaces |  |  | Additional exterior lighting power allowance | Additional exterior lighting power allowance
|  |  | Building facades | No Allowance | No Allowance | No Allowance |  | No Allowance |  | No Allowance
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf |  | 0.50 w/sf |  | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of covered & uncovered area | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through |  | 200 w per drive-through |  | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry |  | 400 w per main entry |  | 400 w per main entry
|  |  | Roadway/parking entry, trail head, & toilet facility, or other locations approved by authority having jurisdiction |  |  |  |  | No additional allowance |  | No additional allowance
|  |  | For areas that are not listed or are not comparable, use comparable interior space type as modified by factors | [6 empty] | 65% of interior lighting power allowance value
Zone 2: areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited night-time use & residential mixed use areas
Zone 2: Tradable surfaces
|  |  | Base site allowance | 600 w | 400 w | 400 w |  | 400 w |  | 400 w
|  |  | Uncovered parking areas and drives | 0.06 w/sf | 0.04 w/sf | 0.04 w/sf |  | 0.04 w/sf |  | 0.04 w/sf
|  |  | Walkways <10 ft wide | 0.7 w/lin ft | 0.5 w/lin ft | 0.50 w/lin ft |  | 0.5 w/lin ft |  | 0.50 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.14 w/sf | 0.10 w/sf | 0.10 w/sf |  | 0.10 w/sf |  | 0.10 w/sf
|  |  | Dining areas |  | 0.65 w/sf | 0.65 w/sf |  | 0.65 w/sf |  | 0.65 w/sf
|  |  | Stairways | 1.0 w/sf | 0.70 w/sf | 0.70 w/sf |  | 0.70 w/sf |  | 0.70 w/sf
|  |  | Pedestrian tunnels | 0.15 w/sf | 0.12 w/sf | 0.12 w/sf |  | 0.12 w/sf |  | 0.12 w/sf
|  |  | Landscaping |  | 0.04 w/sf | 0.04 w/sf |  | 0.04 w/sf |  | 0.04 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 20 w/lin ft of Door Width | 14 w/lin ft of opening | 14 w/lin ft of opening |  | 14 w/lin ft of opening |  | 14 w/lin ft of opening
|  |  | Entry canopies | 0.25 w/sf | 0.25 w/sf | 0.20 w/sf |  | 0.25 w/sf |  | 0.20 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 0.60 w/sf | 0.40 w/sf | 0.40 w/sf |  | 0.40 w/sf |  | 0.40 w/sf
|  |  | Outdoor open sales areas | 0.25 w/sf | 0.20 w/sf | 0.20 w/sf |  | 0.20 w/sf |  | 0.20 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | 10 w/lin ft | 7 w/lin ft | 7 w/lin ft |  | 7 w/lin ft |  | 7 w/lin ft
|  | Zone 2: Non-tradable surfaces |  |  | Additional exterior lighting power allowance | Additional exterior lighting power allowance
|  |  | Building facades | 0.075 w/sf of gross above-grade wall area | 0.075 w/sf of gross above-grade wall area | 0.075 w/sf of gross above-grade wall area |  | 0.1 w/sf of façade area or 2.5 w/lin ft façade length |  | 0.1 w/sf of façade area or 2.5 w/lin ft façade length
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf |  | 0.50 w/sf |  | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of Covered & Uncovered Area | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through |  | 200 w per drive-through |  | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry |  | 400 w per main entry |  | 400 w per main entry
|  |  | Roadway/parking entry, trail head, & toilet facility, or other locations approved by authority having jurisdiction |  |  |  |  | No additional allowance |  | No additional allowance
|  |  | For areas that are not listed or are not comparable, use comparable interior space type as modified by factors | [6 empty] | 65% of interior lighting power allowance value
Zone 3: all other areas
Zone 3: Tradable surfaces
|  |  | Base site allowance | 750 w | 500 w | 500 w |  | 500 w |  | 500 w
|  |  | Uncovered parking areas and drives | 0.10 w/sf | 0.06 w/sf | 0.06 w/sf |  | 0.06 w/sf |  | 0.06 w/sf
|  |  | Walkways <10 ft wide | 0.8 w/lin ft | 0.6 w/lin ft | 0.60 w/lin ft |  | 0.6 w/lin ft |  | 0.60 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.16 w/sf | 0.11 w/sf | 0.11 w/sf |  | 0.11 w/sf |  | 0.11 w/sf
|  |  | Dining areas |  | 0.75 w/sf | 0.75 w/sf |  | 0.75 w/sf |  | 0.75 w/sf
|  |  | Stairways | 1.0 w/sf | 0.7 w/sf | 0.70 w/sf |  | 0.7 w/sf |  | 0.70 w/sf
|  |  | Pedestrian tunnels | 0.2 w/sf | 0.14 w/sf | 0.14 w/sf |  | 0.14 w/sf |  | 0.14 w/sf
|  |  | Landscaping |  | 0.04 w/sf | 0.04 w/sf |  | 0.04 w/sf |  | 0.04 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 30 w/lin ft of Door Width | 21 w/lin ft of opening | 21 w/lin ft of opening |  | 21 w/lin ft of opening |  | 21 w/lin ft of opening
|  |  | Entry canopies | 0.4 w/sf | 0.4 w/sf | 0.40 w/sf |  | 0.4 w/sf |  | 0.20 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 0.8 w/sf | 0.6 w/sf | 0.60 w/sf |  | 0.6 w/sf |  | 0.60 w/sf
|  |  | Outdoor open sales areas | 0.5 w/sf | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.20 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | 10 w/lin ft | 7 w/lin ft | 7 w/lin ft |  | 7 w/lin ft |  | 7 w/lin ft
|  | Zone 3: Non tradable surfaces |  |  | Additional exterior lighting power allowance | Additional exterior lighting power allowance
|  |  | Building facades | 0.113 w/sf of gross above-grade wall area | 0.113 w/sf of gross above-grade wall area | 0.113 w/sf of gross above-grade wall area |  | 0.15 w/sf of façade area or 3.75 w/lin ft façade length |  | 0.15 w/sf of façade area or 3.75 w/lin ft façade length
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf |  | 0.50 w/sf |  | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of covered & uncovered area | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through |  | 200 w per drive-through |  | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry |  | 400 w per main entry |  | 400 w per main entry
|  |  | Roadway/parking entry, trail head, & toilet facility, or other locations approved by authority having jurisdiction |  |  |  |  | No additional allowance |  | No additional allowance
|  |  | For areas that are not listed or are not comparable, use comparable interior space type as modified by factors | [6 empty] | 80% of interior lighting power allowance value
Zone 4: high activity commercial districts in major metropolitan areas as designated by the local jurisdiction
Zone 4: Tradable surfaces
|  |  | Base site allowance | 1300 w | 900 w | 900 w |  | 900 w |  | 900 w
|  |  | Uncovered parking areas and drives | 0.13 w/sf | 0.08 w/sf | 0.08 w/sf |  | 0.08 w/sf |  | 0.08 w/sf
|  |  | Walkways <10 ft wide | 1.0 w/lin ft | 0.7 w/lin ft | 0.70 w/lin ft |  | 0.7 w/lin ft |  | 0.70 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.2 w/sf | 0.14 w/sf | 0.14 w/sf |  | 0.14 w/sf |  | 0.14 w/sf
|  |  | Dining areas |  | 0.95 w/sf | 0.95 w/sf |  | 0.95 w/sf |  | 0.95 w/sf
|  |  | Stairways | 1.0 w/sf | 0.70 w/sf | 0.70 w/sf |  | 0.70 w/sf |  | 0.70 w/sf
|  |  | Pedestrian tunnels | 0.3 w/sf | 0.21 w/sf | 0.21 w/sf |  | 0.21 w/sf |  | 0.21 w/sf
|  |  | Landscaping |  | 0.04 w/sf | 0.04 w/sf |  | 0.04 w/sf |  | 0.04 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 30 w/lin ft of Door Width | 21 w/lin ft of opening | 21 w/lin ft of opening |  | 21 w/lin ft of opening |  | 21 w/lin ft of opening
|  |  | Entry canopies | 0.4 w/sf | 0.4 w/sf | 0.40 w/sf |  | 0.4 w/sf |  | 0.20 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 1.0 w/sf | 0.7 w/sf | 0.70 w/sf |  | 0.7 w/sf |  | 0.70 w/sf
|  |  | Outdoor open sales areas | 0.7 w/sf | 0.5 w/sf | 0.50 w/sf |  | 0.5 w/sf |  | 0.20 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | 30 w/lin ft | 21 w/lin ft | 21 w/lin ft |  | 21 w/lin ft |  | 21 w/lin ft
|  | Zone 4: non-tradable surfaces |  |  | Additional exterior lighting power allowance | Additional exterior lighting power allowance
|  |  | Building facades | 0.15 w/sf of gross above-grade wall area | 0.15 w/sf of gross above-grade wall area | 0.15 w/sf of gross above-grade wall area |  | 0.2 w/sf of façade area or 5.0 w/lin ft façade length |  | 0.2 w/sf of façade area or 5.0 w/lin ft façade length
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location |  | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf |  | 0.50 w/sf |  | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of covered & uncovered area | 0.35 w/sf | 0.35 w/sf |  | 0.35 w/sf |  | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through |  | 200 w per drive-through |  | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry |  | 400 w per main entry |  | 400 w per main entry
|  |  | Roadway/parking entry, trail head, & toilet facility, or other locations approved by authority having jurisdiction |  |  |  |  | No additional allowance |  | No additional allowance
|  |  | For areas that are not listed or are not comparable, use comparable interior space type as modified by factors | [6 empty] | 100% of interior lighting power allowance value
Other Equipment
Minimum Nominal Efficiency for Motors
|  |  |  | 60 HZ General Purpose Electric Motors (Subtype I) | 60 HZ NEMA Design A, NEMA Design B, IEC Design N (excluding fire pump) | 60 HZ NEMA Design A, NEMA Design B, IEC Design N (excluding fire pump) |  | 60 HZ NEMA Design A, NEMA Design B, IEC Design N (excluding fire pump) |  | 60 HZ NEMA Design A, NEMA Design B, IEC Design N (excluding fire pump)
ODP - 3600 rpm (hp)
|  |  | 1 | 77 | 77 | 77 |  | 77 |  | 77
|  |  | 1.5 | 84 | 84 | 84 |  | 84 |  | 84
|  |  | 2 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 3 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 5 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 7.5 | 88.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 10 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 15 | 90.2 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 20 | 91 | 91 | 91 |  | 91 |  | 91
|  |  | 25 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 30 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 40 | 92.4 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 50 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 60 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 75 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 100 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 125 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 150 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 200 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 250 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 300 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 350 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 400 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 450 | 95.8 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 500 | 95.8 | 96.2 | 96.2 |  | 96.2 |  | 96.2
ODP - 1800 rpm (hp)
|  |  | 1 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 91 | 91 | 91 |  | 91 |  | 91
|  |  | 10 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 15 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 20 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 25 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 30 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 40 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 94.5 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 60 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 75 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 100 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 125 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 150 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 200 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 250 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 300 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 350 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 400 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 450 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 500 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
ODP - 1200 rpm (hp)
|  |  | 1 | 82.5 | 82.5 | 82.5 |  | 82.5 |  | 82.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 87.5 | 87.5 | 87.5 |  | 87.5 |  | 87.5
|  |  | 3 | 88.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 5 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 90.2 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 10 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 15 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 20 | 92.4 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 25 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 30 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 40 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 60 | 94.5 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 75 | 94.5 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 100 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 125 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 150 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 200 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 250 | 95.4 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 300 | 95.4 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 350 | 95.4 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 400 | 95.8 | NR | NR |  | NR |  | NR
|  |  | 450 | 96.2 | NR | NR |  | NR |  | NR
|  |  | 500 | 96.2 | NR | NR |  | NR |  | NR
ODP - 900 rpm (hp)
|  |  | 1 |  | 75.5 | 75.5 |  | 75.5 |  | 75.5
|  |  | 1.5 |  | 77 | 77 |  | 77 |  | 77
|  |  | 2 |  | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 |  | 87.5 | 87.5 |  | 87.5 |  | 87.5
|  |  | 5 |  | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 7.5 |  | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 10 |  | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 15 |  | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 20 |  | 91 | 91 |  | 91 |  | 91
|  |  | 25 |  | 91 | 91 |  | 91 |  | 91
|  |  | 30 |  | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 40 |  | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 50 |  | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 60 |  | 93 | 93 |  | 93 |  | 93
|  |  | 75 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 100 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 125 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 150 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 200 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 250 |  | 95 | 95 |  | 95 |  | 95
TEFC - 3600 rpm (hp)
|  |  | 1 | 77 | 77 | 77 |  | 77 |  | 77
|  |  | 1.5 | 84 | 84 | 84 |  | 84 |  | 84
|  |  | 2 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 3 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 5 | 88.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 7.5 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 10 | 90.2 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 15 | 91 | 91 | 91 |  | 91 |  | 91
|  |  | 20 | 91 | 91 | 91 |  | 91 |  | 91
|  |  | 25 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 30 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 40 | 92.4 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 50 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 60 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 75 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 100 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 125 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 150 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 200 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 250 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 300 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 350 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 400 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 450 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 500 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
TEFC - 1800 rpm (hp)
|  |  | 1 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 10 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 15 | 92.4 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 20 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 25 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 30 | 93.6 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 40 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 94.5 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 60 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 75 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 100 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 125 | 95.4 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 150 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 200 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 250 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 300 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 350 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 400 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 450 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 500 | 96.2 | 96.2 | 96.2 |  | 96.2 |  | 96.2
TEFC - 1200 rpm (hp)
|  |  | 1 | 82.5 | 82.5 | 82.5 |  | 82.5 |  | 82.5
|  |  | 1.5 | 87.5 | 87.5 | 87.5 |  | 87.5 |  | 87.5
|  |  | 2 | 88.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 3 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 91 | 91 | 91 |  | 91 |  | 91
|  |  | 10 | 91 | 91 | 91 |  | 91 |  | 91
|  |  | 15 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 20 | 91.7 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 25 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 30 | 93 | 93 | 93 |  | 93 |  | 93
|  |  | 40 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 94.1 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 60 | 94.5 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 75 | 94.5 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 100 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 125 | 95 | 95 | 95 |  | 95 |  | 95
|  |  | 150 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 200 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 250 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 300 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 350 | 95.8 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 400 | 95.8 | NR | NR |  | NR |  | NR
|  |  | 450 | 95.8 | NR | NR |  | NR |  | NR
|  |  | 500 | 95.8 | NR | NR |  | NR |  | NR
TEFC - 900 rpm (hp)
|  |  | 1 |  | 75.5 | 75.5 |  | 75.5 |  | 75.5
|  |  | 1.5 |  | 78.5 | 78.5 |  | 78.5 |  | 78.5
|  |  | 2 |  | 84 | 84 |  | 84 |  | 84
|  |  | 3 |  | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 5 |  | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 7.5 |  | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 10 |  | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 15 |  | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 20 |  | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 25 |  | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 30 |  | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 40 |  | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 50 |  | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 60 |  | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 75 |  | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 100 |  | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 125 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 150 |  | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 200 |  | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 250 |  | 95 | 95 |  | 95 |  | 95
|  |  |  | General Purpose Electric Motors (Subtype II and Design B) | 60 Hz NEMA Design C and IEC Design H Motors | 60 Hz NEMA Design C and IEC Design H Motors |  | 60 Hz NEMA Design C and IEC Design H Motors |  | 60 Hz NEMA Design C and IEC Design H Motors
ODP - 3600 rpm (hp)
|  |  | 1 | NR
|  |  | 1.5 | 82.5
|  |  | 2 | 84
|  |  | 3 | 84
|  |  | 5 | 85.5
|  |  | 7.5 | 87.5
|  |  | 10 | 88.5
|  |  | 15 | 89.5
|  |  | 20 | 90.2
|  |  | 25 | 91
|  |  | 30 | 91
|  |  | 40 | 91.7
|  |  | 50 | 92.4
|  |  | 60 | 93
|  |  | 75 | 93
|  |  | 100 | 93
|  |  | 125 | 93.6
|  |  | 150 | 93.6
|  |  | 200 | 94.5
|  |  | 250 | 94.5
|  |  | 300 | 95
|  |  | 350 | 95
|  |  | 400 | 95.4
|  |  | 450 | 95.8
|  |  | 500 | 95.8
ODP - 1800 rpm (hp)
|  |  | 1 | 82.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 1.5 | 84 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 84 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 | 86.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 5 | 87.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 88.5 | 91 | 91 |  | 91 |  | 91
|  |  | 10 | 89.5 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 15 | 91 | 93 | 93 |  | 93 |  | 93
|  |  | 20 | 91 | 93 | 93 |  | 93 |  | 93
|  |  | 25 | 91.7 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 30 | 92.4 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 40 | 93 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 93 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 60 | 93.6 | 95 | 95 |  | 95 |  | 95
|  |  | 75 | 94.1 | 95 | 95 |  | 95 |  | 95
|  |  | 100 | 94.1 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 125 | 94.5 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 150 | 95 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 200 | 95 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 250 | 95.4
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | 95.4
|  |  | 450 | 95.8
|  |  | 500 | 95.8
ODP - 1200 rpm (hp)
|  |  | 1 | 80 | 82.5 | 82.5 |  | 82.5 |  | 82.5
|  |  | 1.5 | 84 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 85.5 | 87.5 | 87.5 |  | 87.5 |  | 87.5
|  |  | 3 | 86.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 5 | 87.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 88.5 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 10 | 90.2 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 15 | 90.2 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 20 | 91 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 25 | 91.7 | 93 | 93 |  | 93 |  | 93
|  |  | 30 | 92.4 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 40 | 93 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 93 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 60 | 93.6 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 75 | 93.6 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 100 | 94.1 | 95 | 95 |  | 95 |  | 95
|  |  | 125 | 94.1 | 95 | 95 |  | 95 |  | 95
|  |  | 150 | 94.5 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 200 | 94.5 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 250 | 95.4
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
ODP - 900 rpm (hp)
|  |  | 1 | 74 | 75.5 | 75.5 |  | 75.5 |  | 75.5
|  |  | 1.5 | 75.5 | 77 | 77 |  | 77 |  | 77
|  |  | 2 | 85.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 | 86.5 | 87.5 | 87.5 |  | 87.5 |  | 87.5
|  |  | 5 | 87.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 7.5 | 88.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 10 | 89.5 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 15 | 89.5 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 20 | 90.2 | 91 | 91 |  | 91 |  | 91
|  |  | 25 | 90.2 | 91 | 91 |  | 91 |  | 91
|  |  | 30 | 91 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 40 | 91 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 50 | 91.7 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 60 | 92.4 | 93 | 93 |  | 93 |  | 93
|  |  | 75 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 100 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 125 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 150 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 200 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 250 | 94.5
|  |  | 300 | NR
|  |  | 350 | NR
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
TEFC - 3600 rpm (hp)
|  |  | 1 | 75.5
|  |  | 1.5 | 82.5
|  |  | 2 | 84
|  |  | 3 | 85.5
|  |  | 5 | 87.5
|  |  | 7.5 | 88.5
|  |  | 10 | 89.5
|  |  | 15 | 90.2
|  |  | 20 | 90.2
|  |  | 25 | 91
|  |  | 30 | 91
|  |  | 40 | 91.7
|  |  | 50 | 92.4
|  |  | 60 | 93
|  |  | 75 | 93
|  |  | 100 | 93.6
|  |  | 125 | 94.5
|  |  | 150 | 94.5
|  |  | 200 | 95
|  |  | 250 | 95.4
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | 95.4
|  |  | 450 | 95.4
|  |  | 500 | 95.4
TEFC - 1800 rpm (hp)
|  |  | 1 | 82.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 1.5 | 84 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 84 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 | 87.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 5 | 87.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 89.5 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 10 | 89.5 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 15 | 91 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 20 | 91 | 93 | 93 |  | 93 |  | 93
|  |  | 25 | 92.4 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 30 | 92.4 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 40 | 93 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 93 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 60 | 93.6 | 95 | 95 |  | 95 |  | 95
|  |  | 75 | 94.1 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 100 | 94.5 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 125 | 94.5 | 95.4 | 95.4 |  | 95.4 |  | 95.4
|  |  | 150 | 95 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 200 | 95 | 96.2 | 96.2 |  | 96.2 |  | 96.2
|  |  | 250 | 95
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | 95.4
|  |  | 450 | 95.4
|  |  | 500 | 95.8
TEFC - 1200 rpm (hp)
|  |  | 1 | 80 | 82.5 | 82.5 |  | 82.5 |  | 82.5
|  |  | 1.5 | 85.5 | 87.5 | 87.5 |  | 87.5 |  | 87.5
|  |  | 2 | 86.5 | 88.5 | 88.5 |  | 88.5 |  | 88.5
|  |  | 3 | 87.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 5 | 87.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 7.5 | 89.5 | 91 | 91 |  | 91 |  | 91
|  |  | 10 | 89.5 | 91 | 91 |  | 91 |  | 91
|  |  | 15 | 90.2 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 20 | 90.2 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 25 | 91.7 | 93 | 93 |  | 93 |  | 93
|  |  | 30 | 91.7 | 93 | 93 |  | 93 |  | 93
|  |  | 40 | 93 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 50 | 93 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 60 | 93.6 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 75 | 93.6 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 100 | 94.1 | 95 | 95 |  | 95 |  | 95
|  |  | 125 | 94.1 | 95 | 95 |  | 95 |  | 95
|  |  | 150 | 95 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 200 | 95 | 95.8 | 95.8 |  | 95.8 |  | 95.8
|  |  | 250 | 95
|  |  | 300 | 95
|  |  | 350 | 95
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
TEFC - 900 rpm (hp)
|  |  | 1 | 74 | 75.5 | 75.5 |  | 75.5 |  | 75.5
|  |  | 1.5 | 77 | 78.5 | 78.5 |  | 78.5 |  | 78.5
|  |  | 2 | 82.5 | 84 | 84 |  | 84 |  | 84
|  |  | 3 | 84 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 5 | 84 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 7.5 | 85.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 10 | 88.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 15 | 88.5 | 89.5 | 89.5 |  | 89.5 |  | 89.5
|  |  | 20 | 89.5 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 25 | 89.5 | 90.2 | 90.2 |  | 90.2 |  | 90.2
|  |  | 30 | 91 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 40 | 91 | 91.7 | 91.7 |  | 91.7 |  | 91.7
|  |  | 50 | 91.7 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 60 | 91.7 | 92.4 | 92.4 |  | 92.4 |  | 92.4
|  |  | 75 | 93 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 100 | 93 | 93.6 | 93.6 |  | 93.6 |  | 93.6
|  |  | 125 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 150 | 93.6 | 94.1 | 94.1 |  | 94.1 |  | 94.1
|  |  | 200 | 94.1 | 94.5 | 94.5 |  | 94.5 |  | 94.5
|  |  | 250 | 94.5
|  |  | 300 | NR
|  |  | 350 | NR
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
|  |  |  | Polyphase Small Electric Motors | Polyphase Small Electric Motors | Polyphase Small Electric Motors |  | Polyphase Small Electric Motors |  | Polyphase Small Electric Motors
Open Motor - 3600 rpm (hp)
|  |  | 0.25 | 65.6 | 65.6 | 65.6 |  | 65.6 |  | 65.6
|  |  | 0.33 | 69.5 | 69.5 | 69.5 |  | 69.5 |  | 69.5
|  |  | 0.5 | 73.4 | 73.4 | 73.4 |  | 73.4 |  | 73.4
|  |  | 0.75 | 76.8 | 76.8 | 76.8 |  | 76.8 |  | 76.8
|  |  | 1 | 77 | 77 | 77 |  | 77 |  | 77
|  |  | 1.5 | 84 | 84 | 84 |  | 84 |  | 84
|  |  | 2 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
|  |  | 3 | 85.5 | 85.5 | 85.5 |  | 85.5 |  | 85.5
Open Motor - 1800 rpm (hp)
|  |  | 0.25 | 69.5 | 69.5 | 69.5 |  | 69.5 |  | 69.5
|  |  | 0.33 | 73.4 | 73.4 | 73.4 |  | 73.4 |  | 73.4
|  |  | 0.5 | 78.2 | 78.2 | 78.2 |  | 78.2 |  | 78.2
|  |  | 0.75 | 81.1 | 81.1 | 81.1 |  | 81.1 |  | 81.1
|  |  | 1 | 83.5 | 83.5 | 83.5 |  | 83.5 |  | 83.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5 |  | 86.5 |  | 86.5
|  |  | 3 | 86.9 | 86.9 | 86.9 |  | 86.9 |  | 86.9
Open Motor - 1200 rpm (hp)
|  |  | 0.25 | 67.5 | 67.5 | 67.5 |  | 67.5 |  | 67.5
|  |  | 0.33 | 71.4 | 71.4 | 71.4 |  | 71.4 |  | 71.4
|  |  | 0.5 | 75.3 | 75.3 | 75.3 |  | 75.3 |  | 75.3
|  |  | 0.75 | 81.7 | 81.7 | 81.7 |  | 81.7 |  | 81.7
|  |  | 1 | 82.5 | 82.5 | 82.5 |  | 82.5 |  | 82.5
|  |  | 1.5 | 83.8 | 83.8 | 83.8 |  | 83.8 |  | 83.8
|  |  | 2 | N/A | N/A | N/A |  | N/A |  | N/A
|  |  | 3 | N/A | N/A | N/A |  | N/A |  | N/A
|  |  |  | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors |  | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors |  | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors
Open Motor - 3600 rpm (hp)
|  |  | 0.25 | 66.6 | 66.6 | 66.6 |  | 66.6 |  | 66.6
|  |  | 0.33 | 70.5 | 70.5 | 70.5 |  | 70.5 |  | 70.5
|  |  | 0.5 | 72.4 | 72.4 | 72.4 |  | 72.4 |  | 72.4
|  |  | 0.75 | 76.2 | 76.2 | 76.2 |  | 76.2 |  | 76.2
|  |  | 1 | 80.4 | 80.4 | 80.4 |  | 80.4 |  | 80.4
|  |  | 1.5 | 81.5 | 81.5 | 81.5 |  | 81.5 |  | 81.5
|  |  | 2 | 82.9 | 82.9 | 82.9 |  | 82.9 |  | 82.9
|  |  | 3 | 84.1 | 84.1 | 84.1 |  | 84.1 |  | 84.1
Open Motor - 1800 rpm (hp)
|  |  | 0.25 | 68.5 | 68.5 | 68.5 |  | 68.5 |  | 68.5
|  |  | 0.33 | 72.4 | 72.4 | 72.4 |  | 72.4 |  | 72.4
|  |  | 0.5 | 76.2 | 76.2 | 76.2 |  | 76.2 |  | 76.2
|  |  | 0.75 | 81.8 | 81.8 | 81.8 |  | 81.8 |  | 81.8
|  |  | 1 | 82.6 | 82.6 | 82.6 |  | 82.6 |  | 82.6
|  |  | 1.5 | 83.8 | 83.8 | 83.8 |  | 83.8 |  | 83.8
|  |  | 2 | 84.5 | 84.5 | 84.5 |  | 84.5 |  | 84.5
|  |  | 3 | N/A | N/A | N/A |  | N/A |  | N/A
Open Motor - 1200 rpm (hp)
|  |  | 0.25 | 62.2 | 62.2 | 62.2 |  | 62.2 |  | 62.2
|  |  | 0.33 | 66.6 | 66.6 | 66.6 |  | 66.6 |  | 66.6
|  |  | 0.5 | 76.2 | 76.2 | 76.2 |  | 76.2 |  | 76.2
|  |  | 0.75 | 80.2 | 80.2 | 80.2 |  | 80.2 |  | 80.2
|  |  | 1 | 81.1 | 81.1 | 81.1 |  | 81.1 |  | 81.1
|  |  | 1.5 | N/A | N/A | N/A |  | N/A |  | N/A
|  |  | 2 | N/A | N/A | N/A |  | N/A |  | N/A
|  |  | 3 | N/A | N/A | N/A |  | N/A |  | N/A
| Fire Pump Electric Motor Efficiency | [6 empty] | See Table 10.8-5 |  | See Table 10.8-5
|  |  | 1 to 500 hp |  |  |  |  | Generally lower efficiencies |  | Generally lower efficiencies
Maximum Pump Energy Index (PEI)
|  | End suction, close coupled, constant load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | End suction, close coupled, variable load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | End suction, frame mounted, constant load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | End suction, frame mounted, variable load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | In-line, constant load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | In-line, variable load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | Radial split, vertical, constant load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | Radial split, vertical, variable load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | Submersible turbine, constant load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
|  | Submersible turbine, variable load | [7 empty] | Maximum PEI
|  |  | 1800 rpm | [6 empty] | 1
|  |  | 3600 rpm | [6 empty] | 1
Vertical and Horizontal Transportation Systems and Equipment
Elevator cabs
|  |  | Luminaires in each cab | Sum of lumens divided by sum of watts ≥35 | Sum of lumens divided by sum of watts ≥35 | Sum of lumens divided by sum of watts ≥35 |  | Sum of lumens divided by sum of watts ≥35 |  | Sum of lumens divided by sum of watts ≥35
|  |  | Cab ventilation power | ≤0.33 Watts per cfm | ≤0.33 Watts per cfm | ≤0.33 Watts per cfm |  | ≤0.33 Watts per cfm |  | ≤0.33 Watts per cfm
|  |  | Cab standby control | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes |  | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes |  | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes
Escalators and moving walks
|  |  | Automatic controls | To reduce speed to minimum permitted speed when not conveying passengers | To reduce speed to minimum permitted speed when not conveying passengers | To reduce speed to minimum permitted speed when not conveying passengers |  | To reduce speed to minimum permitted speed when not conveying passengers |  | To reduce speed to minimum permitted speed when not conveying passengers
Escalators
|  |  | Designed for one-way down operation or for reverse operation | Have variable frequency regenerative drive that supplies electrical energy to building electrical system when combined weight of passengers ≥750 pounds | Have variable frequency regenerative drive that supplies electrical energy to building electrical system when combined weight of passengers ≥750 pounds | Designed to recover electric energy when resisting overspeed in down direction. Designed to recover, on average, more power than is consumed by the energy recovery feature of its motor controller system.
| Service Water Pressure Booster Systems | [6 empty] | Designed such that: |  | Designed such that:
[8 empty] | Pressure sensors vary speed or start/stop pumps; |  | Pressure sensors vary speed or start/stop pumps;
[8 empty] | No device to reduce water supply pressure; |  | No device to reduce water supply pressure;
[8 empty] | No booster pump operation when no flow |  | No booster pump operation when no flow
| Air curtains | [8 empty] | Installed & commissioned per manufacturer's instructions
|  |  | Jet velocity | [6 empty] | ≥6.6 fps @ 6" above floor
|  |  | Jet direction | [6 empty] | ≤20º toward opening
Whole-Building Energy Monitoring
|  | Monitoring |  |  |  | New Buildings
|  |  | Measurement device for energy use supplied by utility, energy provider or plant not within building |  |  |  |  | Natural gas |  | Natural gas
[8 empty] | Fuel oil |  | Fuel oil
[8 empty] | Propane |  | Propane
[8 empty] | Steam |  | Steam
[8 empty] | Chilled water |  | Chilled water
[8 empty] | Hot water |  | Hot water
Recording and reporting
|  |  | Recorded |  |  | At least every 60 minutes |  | At least every 60 minutes |  | At least every 60 minutes
|  |  | Reported |  |  | Hourly |  | Hourly |  | Hourly
|  |  | (and with capability to create user reports) |  |  | Daily |  | Daily |  | Daily
[6 empty] | Monthly |  | Monthly |  | Monthly
[6 empty] | Annually |  | Annually |  | Annually
|  |  | Retained |  |  | ≥36 months |  | ≥36 months |  | ≥36 months
Exceptions
[6 empty] | New buildings ≤25,000 sf conditioned floor area |  | Buildings or additions <25,000 sf |  | Buildings or additions <25,000 sf
[6 empty] | Individual tenant spaces with own utility services ≤5,000 sf conditioned floor area |  | Individual tenant spaces <10,000 sf |  | Individual tenant spaces <10,000 sf
[8 empty] | Dwelling units |  | Dwelling units
[6 empty] | R-2 occupancies |  | Residential buildings with common areas <10,000 sf |  | Residential buildings with common areas <10,000 sf
[8 empty] | Fuel for on-site emergency equipment |  | Fuel for on-site emergency equipment
Additional Efficiency Package Options (Section C406)
New buildings shall achieve total of 10 additional energy efficiency credits from table based on code section number, use group & climate zone
Where building contains multiple-use groups, credits from each use group shall be weighted by floor area of each use group
Comply with at least one of the following:
|  |  | More efficient HVAC performance | Equipment shall exceed minimum efficiency requirements by ≥10% in addition to requirements listed for Section C403 | Equipment shall exceed minimum efficiency requirements by ≥10% in addition to requirements listed for Section C403
|  |  |  | Where multiple performance requirements are listed, equipment shall exceed all requirements by ≥10% | Where multiple performance requirements are listed, equipment shall exceed all requirements by ≥10%
|  |  |  | Equipment not listed shall be ≤10% of total building system capacity | Equipment not listed shall be ≤10% of total building system capacity
|  |  | Reduced lighting power density | Total interior lighting power of building <90% of lighting power calculated using building area method or space-by-space method | Total interior lighting power of building <90% of lighting power calculated using building area method or space-by-space method
|  |  | Enhanced lighting controls | Interior lighting shall have following enhanced controls located, scheduled and operated in accordance with Section C405.2.2: | Interior lighting shall have following enhanced controls located, scheduled and operated in accordance with Section C405.2.2:
|  |  |  | 1) Luminaires capable of continuous dimming | 1) Luminaires capable of continuous dimming
|  |  |  | 2) Luminaires capable of being addressed individually. Where luminaire class type is not available, controlled group ≤4 luminaires is allowed | 2) Luminaires capable of being addressed individually. Where luminaire class type is not available, controlled group ≤4 luminaires is allowed
|  |  |  | 3) ≤8 luminaires controlled together in a daylight zone | 3) ≤8 luminaires controlled together in a daylight zone
|  |  |  | 4) Fixtures controlled through digital control system that includes: | 4) Fixtures controlled through digital control system that includes:
|  |  |  | 4.1) Control reconfiguration based on digital addressability | 4.1) Control reconfiguration based on digital addressability
|  |  |  | 4.2) Load shedding | 4.2) Load shedding
|  |  |  | 4.3) Individual user control of overhead general illumination in open office | 4.3) Individual user control of overhead general illumination in open office
|  |  |  | 4.4) Occupancy sensors capable of being reconfigured through digital control system | 4.4) Occupancy sensors capable of being reconfigured through digital control system
|  |  |  | 5) Construction documents include submittal of Sequence of Operations, including specifications outlining each function in Item 4 | 5) Construction documents include submittal of Sequence of Operations, including specifications outlining each function in Item 4
|  |  |  | 6) Functional testing of lighting controls per Section C408 | 6) Functional testing of lighting controls per Section C408
|  |  | On-site supply of renewable energy | Total minimum ratings comply with one of: | Total minimum ratings comply with one of:
|  |  |  | ≥0.5 w/sf of Conditioned Floor Area | ≥1.71 Btu/h or ≥0.5 w/sf of conditioned floor area
|  |  |  | ≥3% energy used for mechanical, service water heating and lighting within building | ≥3% energy used for mechanical, service water heating and lighting within building
|  |  | Dedicated outdoor air system for certain HVAC equipment | Independent ventilation system designed to provide ≥100% outdoor air to each individual occupied space as specified by IMC | Independent ventilation system designed to provide ≥100% outdoor air to each individual occupied space as specified by IMC
|  |  |  | Ventilation system capable of total energy recovery | Ventilation system capable of total energy recovery
|  |  |  | Automatic controls for supply-air temperature reset | Automatic controls for supply-air temperature reset
|  |  | Reduced energy use service water heating | Following building types to use this compliance method: | Following building types to use this compliance method:
|  |  |  | Group R-1: Boarding house, hotels or motels | Group R-1: Boarding house, hotels or motels
|  |  |  | Group I-2: Hospitals, psychiatric hospitals & nursing homes | Group I-2: Hospitals, psychiatric hospitals & nursing homes
|  |  |  | Group A-2: Restaurants and banquet halls or buildings containing food preparation areas | Group A-2: Restaurants and banquet halls or buildings containing food preparation areas
|  |  |  | Group F: Laundries | Group F: Laundries
|  |  |  | Group R-2: Buildings with residential occupancies | Group R-2: Buildings with residential occupancies
|  |  |  | Group A-3: Health club & spas | Group A-3: Health club & spas
|  |  |  | Buildings showing service hot water load ≥10% total building energy load | Buildings showing service hot water load ≥10% total building energy load
|  |  |  | One or more of following to provide ≥60% hot water requirements or sized to provide 100% hot water requirements: | One or more of following to provide ≥60% hot water requirements or sized to provide 100% hot water requirements:
|  |  |  | 1) Waste heat recovery | 1) Waste heat recovery
|  |  |  | 2) Solar water-heating system | 2) Solar water-heating system
|  |  | Enhanced envelope performance |  | Designed building total UA ≤85% total UA of code compliant building
|  |  | Reduced air infiltration |  | Verified by whole-building pressurization test conducted by independent third party
≤0.25 cfm/sf air-leakage rate of whole above- & below-grade building envelope @ 0.3"
Exceptions:
Allowed on representative sections ≥25% conditioned floor area for building >250,000 sf
Alternate Compliance |  |  |  | Total Building Performance | Total Building Performance | Total Building Performance |  | Energy Cost Budget Method |  | Energy Cost Budget Method
|  |  |  | Section C407 | Section C407 | Section C407 |  | Section 11 |  | Section 11
[8 empty] | or |  | or
[8 empty] | Appendix G |  | Appendix G
System Commissioning |  |  |  | Section C408 | Section C408 | Section C408 |  | In each section |  | In each section
Use ASHRAE/IES Standard 202 or other generally accepted engineering standard acceptable to building official
| Building operations & maintenance information |  |  |  | Information provided to owner | Information provided to owner |  | Information provided to owner |  | Information provided to owner
[5 empty] | Manufacturers' information, specifications & recommendations | Manufacturers' information, specifications & recommendations
[5 empty] | Programming procedures & data points | Programming procedures & data points
[5 empty] | Narratives | Narratives
[5 empty] | Other illustrative means | Other illustrative means
[5 empty] | Required regular maintenance actions posted on labels | Required regular maintenance actions posted on labels
Building envelope inspection and verification
|  |  | Inspections |  |  |  |  | Fenestration & door requirements |  | Fenestration & door requirements
[8 empty] | Loading dock weatherseals |  | Loading dock weatherseals
[8 empty] | Opaque envelope air tightness requirements |  | Opaque envelope air tightness requirements
[8 empty] | Fenestration |  | Fenestration
|  |  | Verification |  |  |  |  | Building envelope |  | Building envelope
[8 empty] | Air leakage per one of: |  | Air leakage per one of:
[8 empty] | a) Air barrier design & installation |  | a) Air barrier design & installation
[8 empty] | b) Whole-building pressurization testing |  | b) Whole-building pressurization testing
| Mechanical systems and service water-heating systems commissioning and completion requirements | [6 empty] | Submittals & completion requirements
|  |  |  | Construction documents clearly indicate provisions for commissioning and completion requirements | Construction documents clearly indicate provisions for commissioning and completion requirements | Construction documents clearly indicate provisions for commissioning and completion requirements |  | Construction documents shall require HVAC control systems to be tested to ensure control elements are calibrated, adjusted and in proper working conditions for projects >50,000 sf conditioned area except for warehouses & semi-heated spaces |  | Detailed instructions for commissioning HVAC systems shall be provided in construction documents
|  |  |  | Provide evidence of commissioning and completion prior to final inspection | Provide evidence of commissioning and completion prior to final inspection | Provide evidence of commissioning and completion prior to final inspection
|  |  |  | Copies of all documentation given to owner and made available to code official | Copies of all documentation given to owner and made available to code official | Copies of all documentation given to owner and made available to code official
|  |  |  | Exceptions: | Exceptions: | Exceptions: |  | Authority having jurisdiction may require compliance documentation and supplemental information
|  |  |  | 1) Mechanical systems in buildings where total mechanical equipment capacity ≤480,000 Btu/h cooling capacity and ≤600,000 Btu/h heating capacity | 1) Mechanical systems in buildings where total mechanical equipment capacity ≤480,000 Btu/h cooling capacity and ≤600,000 Btu/h heating capacity | 1) Mechanical systems in buildings where total mechanical equipment capacity ≤480,000 Btu/h cooling capacity and ≤600,000 Btu/h combined space and service water heating capacity
|  |  |  | 2) Systems serving individual dwelling units and sleeping units | 2) Systems serving individual dwelling units and sleeping units | 2) Systems serving individual dwelling units and sleeping units
Commissioning plan
|  |  |  | Narrative description of activities during each phase including personnel to accomplish each | Narrative description of activities during each phase including personnel to accomplish each | Narrative description of activities during each phase including personnel to accomplish each |  | ASHRAE Guideline 1.1-2007, HVAC&R Technical Requirements for the Commissioning Process |  | Identify functional performance tests or verification procedures for all systems to be verified, commissioned or tested
|  |  |  | Specific equipment, appliances or systems to be tested and description of test | Specific equipment, appliances or systems to be tested and description of test | Specific equipment, appliances or systems to be tested and description of test
|  |  |  | Functions to be tested, including but not limited to calibration and economizer controls | Functions to be tested, including but not limited to calibration and economizer controls | Functions to be tested, including but not limited to calibration and economizer controls
|  |  |  | Conditions under which test will be performed | Conditions under which test will be performed | Conditions under which test will be performed
|  |  |  | Measurable criteria for performance | Measurable criteria for performance | Measurable criteria for performance
Systems adjusting and balancing
|  |  | Air systems balancing | Required | Required | Required |  | Required |  | Required
|  |  |  | Discharge dampers used for balancing prohibited on fans ≥10 hp | Discharge dampers used for balancing prohibited on fans ≥10 hp | Discharge dampers used for balancing prohibited on fans ≥10 hp |  | First minimize throttling losses then |  | First minimize throttling losses then
|  |  |  | Speed adjusted on fans >1 hp | Speed adjusted on fans >1 hp | Speed adjusted on fans >1 hp |  | Adjust speed on fan systems >1 hp |  | Adjust speed on fan systems >1 hp
|  |  | Hydronic systems balancing | Required | Required | Required |  | Required |  | Required
|  |  |  | Exceptions: | Exceptions: | Exceptions: |  | Exceptions: |  | Exceptions:
|  |  |  | 1) Pump motors ≤5 hp | 1) Pump motors ≤5 hp | 1) Pump motors ≤5 hp |  | 1) Pump motors ≤10 hp |  | 1) Pump motors ≤10 hp
|  |  |  | 2) When throttling results ≤5% nameplate hp draw above that if impeller were trimmed | 2) When throttling results ≤5% nameplate hp draw above that if impeller were trimmed | 2) When throttling results ≤5% nameplate hp draw above that if impeller were trimmed |  | 2) When throttling results ≤5% nameplate hp draw above or 3hpthat if impeller were trimmed |  | 2) When throttling results ≤5% nameplate hp draw above or 3hpthat if impeller were trimmed
Functional performance testing
|  |  | Equipment | Demonstrate installation and operation of components, systems and system-to-system interfacing relationships | Demonstrate installation and operation of components, systems and system-to-system interfacing relationships | Demonstrate installation and operation of components, systems and system-to-system interfacing relationships
|  |  |  | All modes in sequence of operation | All modes in sequence of operation | All modes in sequence of operation
|  |  |  | Redundant or automatic back-up mode | Redundant or automatic back-up mode | Redundant or automatic back-up mode
|  |  |  | Alarm performance | Alarm performance | Alarm performance
|  |  |  | Mode of operation upon loss and restoration of power | Mode of operation upon loss and restoration of power | Mode of operation upon loss and restoration of power
|  |  |  | Exception: unitary or packaged equipment not required to have supply air economizers | Exception: unitary or packaged equipment not required to have supply air economizers | Exception: unitary or packaged equipment not required to have supply air economizers
|  |  | Controls | Document that control devices, components, equipment and systems are calibrated, adjusted and operational | Document that control devices, components, equipment and systems are calibrated, adjusted and operational | Document that control devices, components, equipment and systems are calibrated, adjusted and operational |  | Tested to ensure that control elements are calibrated, adjusted, & in proper working condition |  | Tested to ensure that control elements are calibrated, adjusted, configured and operating in accordance with applicable requirements
|  |  |  | Determine air economizers operate | Determine air economizers operate | Determine air economizers operate
|  | Preliminary commissioning report |  | Completed and provided to owner | Completed and provided to owner | Completed and provided to owner |  |  |  | Completed and provided to owner
|  |  |  | Mechanical and service hot water findings in separate sections | Mechanical and service hot water findings in separate sections | Mechanical and service hot water findings in separate sections |  |  |  | Required performance of equipment, systems & assemblies, and results of functional performance tests & verification
|  |  |  | Itemize deficiencies found but not corrected at time of report | Itemize deficiencies found but not corrected at time of report | Itemize deficiencies found but not corrected at time of report |  |  |  | Summary of compliance of building & its components, assemblies, controls and systems with required provisions of this standard
|  |  |  | Identify deferred tests that could not be performed because of climate conditions | Identify deferred tests that could not be performed because of climate conditions | Identify deferred tests that could not be performed because of climate conditions |  |  |  | Issues & resolution logs including itemization of deficiencies found during verification, testing & commissioning that have not been corrected at time of report
|  |  |  | Climate conditions required for deferred tests | Climate conditions required for deferred tests | Climate conditions required for deferred tests |  |  |  | Deferred test
|  |  |  | Results of functional performance tests | Results of functional performance tests | Results of functional performance tests |  |  |  | Documentation of training of operating personnel & building occupants and plan for completion of any deferred training
|  |  |  | Functional performance test procedures | Functional performance test procedures | Functional performance test procedures |  |  |  | Plan for completion of commissioning and training, including climatic conditions for deferred test
|  |  |  | Letter from owner to code official acknowledging receipt of report prior to final inspection | Copy of report given to code official by owner prior to final inspection | Copy of report given to code official by owner prior to final inspection
|  |  |  | Code official permitted to require a copy for review | Code official permitted to have report made available for review | Code official permitted to have report made available for review
|  | Documentation requirements |  | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal within 90 days of Certificate of Occupancy |  | Construction documents to require submittal of record drawings within 90 days of system acceptance |  | Construction documents to require submittal of record drawings within 90 days of system acceptance
|  |  | Drawings | Location and performance data of each piece of equipment requiring maintenance |  |  |  | Location and performance data of each piece of equipment requiring maintenance |  | Location and performance data of each piece of equipment requiring maintenance
[8 empty] | General configuration of duct & pipe distribution system, including sizes |  | General configuration of duct & pipe distribution system, including sizes
[8 empty] | Terminal air or water design flow rates |  | Terminal air or water design flow rates
|  |  | Manuals (operating manual and maintenance manual) | Submittal data for each piece of equipment requiring maintenance |  |  |  | Submittal data for each piece of equipment requiring maintenance |  | Submittal data for each piece of equipment requiring maintenance
|  |  |  | Manufacturer's operation manuals and maintenance manuals for each piece of equipment requiring maintenance |  |  |  | Manufacturer's operation manuals and maintenance manuals for each piece of equipment requiring maintenance |  | Manufacturer's operation manuals and maintenance manuals for each piece of equipment requiring maintenance
|  |  |  | Name and address of service agency |  |  |  | Name and address of service agency |  | Name and address of service agency
|  |  |  | Control system maintenance and calibration information including wiring diagrams, schematics and control sequence descriptions |  |  |  | Control system maintenance and calibration information including wiring diagrams, schematics and control sequence descriptions |  | Control system maintenance and calibration information including wiring diagrams, schematics and control sequence descriptions
|  |  |  | Desired or field-determined set points |  |  |  | Desired or field-determined set points |  | Desired or field-determined set points
|  |  |  | Narrative of how each system is intended to operate |  |  |  | Narrative of how each system is intended to operate |  | Narrative of how each system is intended to operate
|  |  | System balancing report | Written report describing activities and measurements | Written report describing activities and measurements | Written report describing activities and measurements |  | Written report for HVAC systems serving zones with total conditioned area >5,000 sf |  | Written report for HVAC systems serving zones with total conditioned area >5,000 sf
|  | Final commissioning report |  | Completed and provided to owner | Completed and provided to owner | Completed and provided to owner |  | Completed and provided to owner |  | Completed and provided to owner
|  |  |  | Mechanical and service hot water findings in separate sections | Mechanical and service hot water findings in separate sections | Mechanical and service hot water findings in separate sections
|  |  |  | Results of functional performance tests | Results of functional performance tests | Results of functional performance tests
|  |  |  | Disposition of deficiencies found during testing including details of corrective measures used or proposed | Disposition of deficiencies found during testing including details of corrective measures used or proposed | Disposition of deficiencies found during testing including details of corrective measures used or proposed
|  |  |  | Functional performance test procedures including measurable criteria for test acceptance | Functional performance test procedures including measurable criteria for test acceptance | Functional performance test procedures including measurable criteria for test acceptance
|  |  |  | Exception: Deferred tests that could not be performed at time of report preparation due to climate conditions | Exception: Deferred tests that could not be performed at time of report preparation due to climate conditions | Exception: Deferred tests that could not be performed at time of report preparation due to climate conditions
| Power commissioning and completion requirements | [6 empty] | Submittals |  | Submittals
|  |  | Drawings |  |  |  |  | Construction documents to require submittal of record drawings within 30 days of system acceptance |  | Construction documents to require submittal of record drawings within 90 days of system acceptance
[8 empty] | Single-line diagram of building electrical distribution system |  | Single-line diagram of building electrical distribution system
[8 empty] | Location and area served for all distribution |  | Location and area served for all distribution
|  |  | Manuals (operating manual and maintenance manual) |  |  |  |  | Submittal data for each piece of equipment requiring maintenance |  | Submittal data for each piece of equipment requiring maintenance
[8 empty] | Operation manuals and maintenance manuals for each piece of equipment requiring maintenance with routine maintenance actions clearly identified |  | Operation manuals and maintenance manuals for each piece of equipment requiring maintenance with routine maintenance actions clearly identified
[8 empty] | Name and address of service agency |  | Name and address of service agency
[8 empty] | Narrative of how each system is intended to operate |  | Narrative of how each system is intended to operate
| Lighting systems commissioning and completion requirements | [6 empty] | Submittals - Completion Requirements |  | Submittals - Completion Requirements
|  | Documentation requirements |  | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal within 90 days of Certificate of Occupancy |  | Construction documents to require submittal of record drawings within 90 days of system acceptance |  | Construction documents to require submittal of record drawings within 90 days of system acceptance
[8 empty] | Design documents to identify all luminaires for general lighting located within: |  | Design documents to identify all luminaires for general lighting located within:
[8 empty] | Daylight areas under skylights |  | Daylight areas under skylights
[8 empty] | Daylight areas under roof monitors |  | Daylight areas under roof monitors
[8 empty] | Primary sidelighted areas |  | Primary sidelighted areas
[8 empty] | Secondary sidelighted areas |  | Secondary sidelighted areas
|  |  | Drawings |  | Location & catalog number of each piece of equipment | Location & catalog number of each piece of equipment |  | Location, luminaire identifier, control and circuiting for each piece of lighting equipment |  | Location, luminaire identifier, control and circuiting for each piece of lighting equipment
[8 empty] | Identification of all luminaires for general lighting in daylight zones |  | Identification of all luminaires for general lighting in daylight zones
|  |  | Manuals | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls |  |  |  | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls |  | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls
|  |  |  | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions, cleaning and recommended relamping | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions, cleaning and recommended relamping | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions, cleaning and recommended relamping |  | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions and recommended relamping/cleaning program |  | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions and recommended relamping/cleaning program
|  |  |  | Inspection and recalibration schedules for all lighting controls | Inspection and recalibration schedules for all lighting controls | Inspection and recalibration schedules for all lighting controls |  | Inspection and recalibration schedules for all lighting controls |  | Inspection and recalibration schedules for all lighting controls
|  |  |  | Narrative of how each system is intended to operate including recommended settings | Narrative of how each system is intended to operate including recommended settings | Narrative of how each system is intended to operate including recommended settings |  | Narrative of how each system is intended to operate including recommended settings |  | Narrative of how each system is intended to operate including recommended settings
|  | Functional testing |  | Provide evidence of commissioning prior to final inspection | Provide evidence of commissioning prior to final inspection | Provide evidence of commissioning prior to final inspection |  | Control devices & systems tested to ensure control hardware & software are calibrated, adjusted, programmed & in proper working condition |  | Control devices & systems tested to ensure control hardware & software are calibrated, adjusted, programmed & in proper working condition
|  |  | Occupant sensor controls | Certify that sensors have been located and aimed | Certify that sensors have been located and aimed | Certify that sensors have been located and aimed |  | Certify that sensors have been located and aimed |  | Certify that sensors have been located and aimed
|  |  |  | Test all sensors for projects with ≤7 sensors | Test all sensors for projects with ≤7 sensors | Test all sensors for projects with ≤7 sensors |  | Test all sensors for projects with ≤7 sensors |  | Test all sensors for projects with ≤7 sensors
|  |  |  | For projects with >7 sensors, test each unique combination of sensor type and space geometry | For projects with >7 sensors, test each unique combination of sensor type and space geometry | For projects with >7 sensors, test each unique combination of sensor type and space geometry |  | For projects with >7 sensors, test each unique combination of sensor type and space geometry |  | For projects with >7 sensors, test each unique combination of sensor type and space geometry
|  |  |  | Test ≥10% of each combination | Test ≥10% of each combination | Test ≥10% of each combination
|  |  |  | Where ≥30% controls fail, test all of identical combination | Where ≥30% controls fail, test all of identical combination | Where ≥30% controls fail, test all of identical combination
|  |  |  | Test to verify | Test to verify | Test to verify |  | Test to verify |  | Test to verify
|  |  |  | 1) Status indicator operation | 1) Status indicator operation | 1) Status indicator operation |  | 1) Status indicator operation |  | 1) Status indicator operation
|  |  |  | 2) Turn off or down to permitted level within required time | 2) Turn off or down to permitted level within required time | 2) Turn off or down to permitted level within required time |  | 2) Turn off or down to permitted level within required time |  | 2) Turn off or down to permitted level within required time
|  |  |  | 3) Auto-on to permitted level | 3) Auto-on to permitted level | 3) Auto-on to permitted level |  | 3) Auto-on to permitted level |  | 3) Auto-on to permitted level
|  |  |  | 4) Manual-on function | 4) Manual-on function | 4) Manual-on function |  | 4) Manual-on function |  | 4) Manual-on function
|  |  |  | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation |  | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation |  | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation
|  |  | Time-switch controls | Confirm accurate programming for weekday, weekend and holiday schedules | Confirm accurate programming for weekday, weekend and holiday schedules | Confirm accurate programming for weekday, weekend and holiday schedules |  | Confirm accurate programming for weekday, weekend and holiday schedules |  | Confirm accurate programming for weekday, weekend and holiday schedules
|  |  |  | Provide documentation to owner of programming | Provide documentation to owner of programming | Provide documentation to owner of programming |  | Provide documentation to owner of programming |  | Provide documentation to owner of programming
|  |  |  | Verify correct time and date | Verify correct time and date | Verify correct time and date |  | Verify correct time and date |  | Verify correct time and date
|  |  |  | Verify any battery back-up is installed and energized | Verify any battery back-up is installed and energized | Verify any battery back-up is installed and energized |  | Verify any battery back-up is installed and energized |  | Verify any battery back-up is installed and energized
|  |  |  | Verify override time limit ≤2 hours | Verify override time limit ≤2 hours | Verify override time limit ≤2 hours |  | Verify override time limit ≤2 hours |  | Verify override time limit ≤2 hours
|  |  |  | Simulate occupied condition | Simulate occupied condition | Simulate occupied condition |  | Simulate occupied condition |  | Simulate occupied condition
|  |  |  | 1) All lights operated by respective area control switch | 1) All lights operated by respective area control switch | 1) All lights operated by respective area control switch |  | 1) All lights operated by respective area control switch |  | 1) All lights operated by respective area control switch
|  |  |  | 2) Switch only operates lighting in enclosed space in which located | 2) Switch only operates lighting in enclosed space in which located | 2) Switch only operates lighting in enclosed space in which located |  | 2) Switch only operates lighting in enclosed space in which located |  | 2) Switch only operates lighting in enclosed space in which located
|  |  |  | Simulate unoccupied condition | Simulate unoccupied condition | Simulate unoccupied condition |  | Simulate unoccupied condition |  | Simulate unoccupied condition
|  |  |  | 1) Nonexempt lighting turns off | 1) Nonexempt lighting turns off | 1) Nonexempt lighting turns off |  | 1) Nonexempt lighting turns off |  | 1) Nonexempt lighting turns off
|  |  |  | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs |  | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs |  | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs
|  |  | Daylight responsive controls | Verify devices proper location, calibration and accurate setpoints and threshold light levels | Verify devices proper location, calibration and accurate setpoints and threshold light levels | Verify devices proper location, calibration and accurate setpoints and threshold light levels |  | Verify devices proper location, calibration and accurate setpoints and threshold light levels |  | Verify devices proper location, calibration and accurate setpoints and threshold light levels
|  |  |  | Verify lighting load adjustments in response to available daylight | Verify lighting load adjustments in response to available daylight | Verify lighting load adjustments in response to available daylight |  | Verify lighting load adjustments in response to available daylight |  | Verify lighting load adjustments in response to available daylight
|  |  |  | Locations of equipment adjustment are readily accessible only to authorized personnel | Locations of equipment adjustment are readily accessible only to authorized personnel | Locations of equipment adjustment are readily accessible only to authorized personnel |  | Locations of equipment adjustment are readily accessible only to authorized personnel |  | Locations of equipment adjustment are readily accessible only to authorized personnel

## Residential
Comparison of Residential Building Performance Characteristics Between |  |  |  | Residential | Residential | Residential
2015 and 2018 International Energy Conservation Code |  |  |  | Provisions | Provisions | Provisions
For Climate Zone 5A |  |  |  | 2015 IECC | 2018 IECC | 2021 IECC
Administration
| Intent and Scope |  |  | Regulate the design and construction of buildings for effective use and conservation of energy over useful life of each building | Regulate the design and construction of buildings for effective use and conservation of energy over useful life of each building | Regulate the design and construction of buildings for effective use and conservation of energy over useful life of each building
|  |  |  | Applies to residential buildings and buildings sites and associated systems and equipment | Applies to residential buildings and buildings sites and associated systems and equipment | Applies to residential buildings and buildings sites and associated systems and equipment
| Applicability / Compliance |  |  | Project shall comply with one of: | Project shall comply with one of: | Project shall comply with one of:
|  |  |  | 1) This code | 1) This code | 1) Prescriptive compliance with one additional efficiency package option installed
|  |  |  | 2) Simulated performance alternative plus mandatory requirements of this code | 2) Simulated performance alternative plus mandatory requirements of this code | 2) Total Building Performance option meeting one of :
One additional efficiency package option installed without including measure in proposed design or
Proposed design with annual energy cost ≤95% annual energy cost of standard reference design
|  |  |  | 3) Energy rating index (ERI) approach | 3) Energy rating index (ERI) approach | 3) Energy rating index (ERI) approach with ≥5% reduction in ERI value.
|  |  | Additions | Chapter 5 | Chapter 5 | Chapter 5
|  |  | Alterations | Chapter 5 | Chapter 5 | Chapter 5
|  |  | Change of occupancy | Chapter 5 | Chapter 5 | Chapter 5
|  |  | Change in space conditioning | Chapter 5 | Chapter 5 | Chapter 5
Certificate (Mandatory)
| Completed certificate |  |  | Posted on wall in space near furnace, utility room or approved location | Posted on wall in space near furnace, utility room or approved location | Posted on wall in space near furnace, utility room or approved location
|  |  |  | Where located on electrical panel, certificate not to cover or obstruct visibility of circuit directory or other required labels | Where located on electrical panel, certificate not to cover or obstruct visibility of circuit directory or other required labels | Where located on electrical panel, certificate not to cover or obstruct visibility of circuit directory or other required labels
Building Envelope |  |  |  | Climate Zone 5A | Climate Zone 5A | Climate Zone 5A
Insulation and fenestration requirements by component
|  |  | Fenestration U-factor | 0.32 | 0.3 | 0.3
|  |  | Skylight U-factor | 0.55 | 0.55 | 0.55
|  |  | Glazed fenestration SHGC | NR | NR | 0.4
|  |  | Ceiling R-value | 49 | 49 | 60
|  |  | Wood frame wall R-value | 20 or 13 + 5ci | 20 or 13 + 5ci | 20 + 5ci or 13 + 10ci or 0 + 15ci
|  |  | Mass wall R-value | 13/17 | 13/17 | 13/17
|  |  | Floor R-value | 30 | 30 | 30
|  |  | Basement wall R-value | 15/19 | 15/19 | 15ci or 19 or 13 + 5ci
|  |  | Slab R-value & depth (unheated) | 10, 2 ft | 10, 2 ft | 10ci, 4 ft
|  |  | Slab R-value & depth (heated) | 15, 2 ft | R-10 to bottom of slab & | R-10 to bottom of slab &
[5 empty] | R-5 under full slab | R-5 under full slab
|  |  | Crawl space wall R-value | 15/19 | 15/19 | 15ci or 19 or 13 + 5ci
U-factor alternative
|  |  | Fenestration U-factor | 0.32 | 0.3 | 0.3
|  |  | Skylight U-factor | 0.55 | 0.55 | 0.55
|  |  | Glazed fenestration SHGC |  |  | NR
|  |  | Ceiling U-factor | 0.026 | 0.026 | 0.024
|  |  | Frame wall U-factor | 0.06 | 0.06 | 0.045
|  |  | Mass wall U-factor | 0.082 | 0.082 | 0.082
|  |  | Floor U-factor | 0.033 | 0.033 | 0.033
|  |  | Basement wall U-factor | 0.05 | 0.05 | 0.05
|  |  | Crawl space wall U-factor | 0.055 | 0.055 | 0.055
Total UA alternative
|  |  | Total building envelope | Proposed UA ≤ UA using table values | Proposed UA ≤ UA using table values | Proposed UA ≤ UA using table values
Specific insulation requirements (Prescriptive)
|  | Ceilings with attic space |  | R-38 deemed to comply for R-49 wherever full height insulation extends over top plate at eaves | R-38 deemed to comply for R-49 wherever full height insulation extends over top plate at eaves | R-49 deemed to comply for R-60 wherever full height insulation over top plate at eaves
|  | Ceilings without attic space |  | R-30 that fits into roof/ceiling space and is limited to ≤500 sf or ≤20% total insulated ceiling, whichever is less | R-30 that fits into roof/ceiling space and is limited to ≤500 sf or ≤20% total insulated ceiling, whichever is less | R-30 that fits into roof/ceiling space and is limited to ≤500 sf or ≤20% total insulated ceiling, whichever is less
|  | Eave baffle |  | Required for air permeable insulation in vented attic | Required for air permeable insulation in vented attic | Required for air permeable insulation in vented attic
|  | Access hatches & doors |  | Weatherstripped & insulated to equivalent insulation on surrounding surfaces | Weatherstripped & insulated to equivalent insulation on surrounding surfaces | Weatherstripped & insulated to equivalent insulation on surrounding surfaces
Exceptions
|  |  | Vertical doors |  |  | U-0.30
|  |  | Horizontal pull-down hatches |  |  | Hatch avg ≤U-0.10 or ≥R-10,
≥75% panel area has ≥R-13,
Net framed opening ≤13.5 sf,
Perimeter weatherstripped
Steel-frame assemblies
|  |  | Steel truss ceilings | R-38 + 5 | R-38 + 5 | Calculated U-factor ≤0.024
|  |  | Steel joist ceiling | R-49 in 2×4 or 2×6 or 2×8 or 2×10 | R-49 in 2×4 or 2×6 or 2×8 or 2×10 | Calculated U-factor ≤0.024
|  |  | Steel-framed wall 16" oc | R-0 + 14.0 or | R-0 + 14.0 or | R-13 + 12.7 or
|  |  |  | R-13 + 8.9 or | R-13 + 8.9 or | R-15 + 12.3 or
|  |  |  | R-15 + 8.5 or | R-15 + 8.5 or | R-19 + 11.6 or
|  |  |  | R-19 + 7.8 or | R-19 + 7.8 or | R-21 + 11.3 or
|  |  |  | R-19 + 6.2 or | R-19 + 6.2 or | R-25 + 10.9
|  |  |  | R-21 + 7.5 | R-21 + 7.5
|  |  | Steel-framed wall 24" oc | R-0 + 14 or | R-0 + 14 or | R-13 + 11.5 or
|  |  |  | R-13 + 7.7 or | R-13 + 7.7 or | R-15 + 10.9 or
|  |  |  | R-15 + 7.1 or | R-15 + 7.1 or | R-19 +10.1 or
|  |  |  | R-19 + 6.3 or | R-19 + 6.3 or | R-21 + 9.7 or
|  |  |  | R-21 + 5.9 | R-21 + 5.9 | R-25 + 9.1
|  |  | Steel joist floors | R-19 + 6 in 2×6 or | R-19 + 6 in 2×6 or | Calculated U-factor ≤0.033
|  |  |  | R-19 12 in 2×8 or | R-19 12 in 2×8 or
|  |  |  | R-19 +12 in 2×10 | R-19 +12 in 2×10
|  | Walls with partial structural sheathing |  | Continuous insulation permitted to be reduced ≤R-3 for consistent total sheathing thickness | Continuous insulation permitted to be reduced ≤R-3 for consistent total sheathing thickness
where structural sheathing covers ≤40% gross area of all exterior walls
|  | Floors |  |  |  | Insulation installed to maintain permanent contact with underside or subfloor
Floor framing cavity insulation permitted to contact top of sheathing separating cavity & unconditioned space below. Perimeter floor framing insulation extended from bottom to top & air sealed.
Combination cavity & continuous insulation installed that cavity insulation in contact with top side of continuous insulation that is installed on underside of floor framing.
|  | Basement walls |  | Top of wall to 10' below grade or to basement floor | Top of wall to 10' below grade or to basement floor | Top of wall to 10' below grade or to basement floor
|  |  |  | Unconditioned basement walls to be insulated unless floor overhead is insulated | Unconditioned basement walls to be insulated unless floor overhead is insulated | Exception for basement walls associated with unconditioned basements where all below are met
Floor overhead, including underside of stair stringers is insulated
NO uninsulated HVAC ducts or pipes or domestic hot water pipes exposed to basement
NO HVAC supply or return diffusers serving basement
Insulated walls surrounding stairway and adjacent conditioned space
Doors leading to basement from conditioned space are insulated and weatherstripped
Compliant building thermal envelope separates basement from adjacent conditioned spaces
|  | Slab-on-grade floors |  | Floor surface <12" below grade | Floor surface <12" below grade | Floor surface <12" below grade
|  |  |  | Top of slab to 24" below grade by any combination of vertical & horizontal | Top of slab to 24" below grade by any combination of vertical & horizontal | Top of slab to 48" below grade by any combination of vertical & horizontal
|  |  |  | Extending away protected by pavement or 10" soil | Extending away protected by pavement or 10" soil | Extending away protected by pavement or 10" soil
|  | Crawl space walls |  | Not vented to outside | Not vented to outside | Not vented to outside
|  |  |  | Downward from floor to finish grade level & then vertically and/or horizontally additional ≥24" | Downward from floor to finish grade level & then vertically and/or horizontally additional ≥24" | Downward from floor to finish grade level & then vertically and/or horizontally additional ≥24"
|  |  |  | Exposed earth covered by Class I vapor retarder | Exposed earth covered by Class I vapor retarder | Exposed earth covered by Class I vapor retarder
|  | Sunroom insulation |  |  |  | and heated garage insulation
|  |  |  | Meet code requirements | Meet code requirements | Meet code requirements
|  |  |  | Exception for thermally isolated conditioned spaces | Exception for thermally isolated conditioned spaces | Exception for thermally isolated conditioned spaces
|  |  |  | ≥R-24 ceiling insulation | ≥R-24 ceiling insulation | ≥R-24 ceiling insulation
|  |  |  | ≥R-13 wall insulation | ≥R-13 wall insulation | ≥R-13 wall insulation
|  |  |  | Wall(s) separating sunroom from conditioned space shall meet building thermal envelope requirement | Wall(s) separating sunroom from conditioned space shall meet building thermal envelope requirement | Wall(s) separating sunroom & garage from conditioned space shall meet building thermal envelope requirement
Fenestration (Prescriptive)
|  | U-factor |  | Area-weighted average permitted | Area-weighted average permitted | Area-weighted average permitted
|  | Glazed fenestration exemption |  | ≤15 sf per dwelling unit exempted from U-factor requirement | ≤15 sf per dwelling unit exempted from U-factor requirement | ≤15 sf per dwelling unit exempted from U-factor requirement
|  | Opaque door exemption |  | One side-hinged ≤24 sf exempt from U-factor requirement | One side-hinged ≤24 sf exempt from U-factor requirement | One side-hinged ≤24 sf exempt from U-factor requirement
|  | Sunroom U-factor |  |  |  | and heated garage
|  |  |  | Exception for thermally isolated conditioned space | Exception for thermally isolated conditioned space | Exception for thermally isolated conditioned space
|  |  | Fenestration | ≤U-0.45 | ≤U-0.45 | ≤U-0.45
|  |  | Skylight | ≤U-0.70 | ≤U-0.70 | ≤U-0.70
|  |  | New fenestration separating sunroom from conditioned space | ≤U-0.32 | ≤U-0.30 | ≤U-0.30
|  | Replacement fenestration (some or all of existing fenestration) |  | ≤U-0.32 | ≤U-0.30 | ≤U-0.30
|  |  |  | In Existing Building Alterations Section | In Existing Building Alterations Section | In Existing Building Alterations Section
Air Leakage (Mandatory)
|  | Sealing methods between dissimilar materials |  | Allow for differential expansion and contraction | Allow for differential expansion and contraction | Allow for differential expansion and contraction
|  | Installation |  | Per manufacturer's instructions | Per manufacturer's instructions | Per manufacturer's instructions
|  |  |  | Per air barrier and insulation installation criteria listed Table R402.4.1.1 | Per air barrier and insulation installation criteria listed Table R402.4.1.1 | Per air barrier and insulation installation criteria listed Table R402.4.1.1
|  | Testing |  | Performed at any time after creation of all penetrations of thermal envelope | Performed at any time after creation of all penetrations of thermal envelope | Performed at any time after creation of all penetrations of thermal envelope
≤5 ach under any compliance path
|  |  |  | ≤3 ach | ≤3 ach | ≤3.0 ach leakage rate
|  |  |  | Provide written report signed by party conducting test | Provide written report signed by party conducting test | Visual inspection permitted for thermally isolated heated garage
|  | Fireplaces |  | New wood-burning | New wood-burning | New wood-burning
|  |  |  | Tight-fitting flue dampers or doors | Tight-fitting flue dampers or doors | Tight-fitting flue dampers or doors
|  |  |  | Outdoor combustion air | Outdoor combustion air | Outdoor combustion air
Fenestration air leakage
|  |  | Windows, skylights & sliding glass doors | ≤0.3 cfm/sf | ≤0.3 cfm/sf | ≤0.3 cfm/sf
|  |  | Swinging doors | ≤0.5 cfm/sf | ≤0.5 cfm/sf | ≤0.5 cfm/sf
|  |  | Exemption: | Site-built windows, skylights & doors | Site-built windows, skylights & doors | Site-built windows, skylights & doors
|  | Rooms containing fuel-burning appliances |  | Where open combustion air ducts provide combustion air to open combustion fuel-burning appliances | Where open combustion air ducts provide combustion air to open combustion fuel-burning appliances | Where open combustion air ducts provide combustion air to open combustion fuel-burning appliances
|  |  | Location of appliances and combustion air opening | Outside of building thermal envelope or | Outside of building thermal envelope or | Outside of building thermal envelope or
|  |  |  | Enclosed in room isolated from inside thermal envelope | Enclosed in room isolated from inside thermal envelope | Enclosed in room isolated from inside thermal envelope
|  |  | Enclosed rooms containing fuel-burning appliances | Doors fully gasketed | Doors fully gasketed | Doors fully gasketed
|  |  |  | Water lines & ducts insulated | Water lines & ducts insulated | Water lines & ducts insulated
|  |  |  | ≥R-8 insulation on combustion air duct | ≥R-8 insulation on combustion air duct | ≥R-8 insulation on combustion air duct
|  |  |  | Insulated to envelope requirements but not less than basement wall R-value | Insulated to envelope requirements but not less than basement wall R-value | Insulated to envelope requirements but not less than basement wall R-value
|  |  | Exceptions | Direct vent appliances with both intake and exhaust pipes to outside | Direct vent appliances with both intake and exhaust pipes to outside | Direct vent appliances with both intake and exhaust pipes to outside
|  |  |  | Code compliant fireplaces and stoves | Code compliant fireplaces and stoves | Code compliant fireplaces and stoves
|  | Recessed lighting (in thermal envelope) |  | Sealed between housing & interior wall or ceiling covering | Sealed between housing & interior wall or ceiling covering | Sealed between housing & interior wall or ceiling covering
|  |  |  | IC-rated | IC-rated | IC-rated
|  |  |  | ≤2.0 cfm air leakage rate | ≤2.0 cfm air leakage rate | ≤2.0 cfm air leakage rate
|  | Electrical and communication outlet boxes (air-sealed boxes) |  |  |  | Sealed to limit air leakage
≤2.0 cfm air leakage rate
Installed per manufacturer's instructions with any required components
Maximum area-weighted average using tradeoffs (Mandatory)
|  |  | Vertical fenestration | U-0.48 | U-0.48 | U-0.48
|  |  | Skylights | U-0.75 | U-0.75 | U-0.75
Systems
| Controls (Mandatory) |  |  | ≥1 for each separate heating & cooling system | ≥1 for each separate heating & cooling system | ≥1 for each separate heating & cooling system
|  | Programmable thermostat |  | Controls primary heating and cooling system | Controls primary heating and cooling system | Controls primary heating and cooling system
|  |  |  | Capabilities: | Capabilities: | Capabilities:
|  |  |  | Daily schedule | Daily schedule | Different daily schedules per day
|  |  |  | Setback or temporarily operate system | Setback or temporarily operate system | Setback or temporarily operate system
|  |  |  | Maintain zone temperature between 55°F & 85°F | Maintain zone temperature between 55°F & 85°F | Maintain zone temperature between 55°F & 85°F
|  | Heat pump supplementary electric resistance heat (Mandatory) |  | Prevent resistance heat operation when compressor can meet heating load | Prevent resistance heat operation when compressor can meet heating load | Prevent resistance heat operation when compressor can meet heating load
|  | Hot water boiler outdoor temperature setback |  | Supply heat to building through one- or two-pipe systems | Supply heat to building through one- or two-pipe systems | Lowers water temperature based on outdoor reset, indoor reset or water temperature sensing
|  |  |  | Lowers water temperature based on outdoor temperature | Lowers water temperature based on outdoor temperature
Ducts
Insulation (Prescriptive)
|  |  | Supply and return ducts in ≥3" outside conditioned space |  |  | ≥R-8
|  |  | Supply and return ducts in <3" outside conditioned space |  |  | ≥R-6
|  |  | Supply and return ducts in ≥3" diameter in attic | ≥R-8 | ≥R-8
|  |  | Supply and return ducts in <3" diameter in attic | ≥R-6 | ≥R-6
|  |  | Supply and return ducts in ≥3" diameter in other areas | ≥R-6 | ≥R-6
|  |  | Supply and return ducts in <3" diameter in other areas | ≥R-4.2 | ≥R-4.2
|  |  | Exemption: | Ducts or portion thereof inside thermal envelope | Ducts or portion thereof inside thermal envelope
|  |  | Ducts buried beneath building |  |  | Per this section or equivalent thermal distribution efficiency
|  |  | Ducts located in conditioned space |  | Comply with either to be considered | Completely located within continuous air barrier and within building thermal envelope
1) Completely within continuous air barrier & within building thermal envelope
2) Buried within ceiling insulation, all of following:
2.1) Air handler located completely within continuous air barrier & building thermal envelope
2.2) Total system duct leakage ≤1.5 cfm per 100 sf
2.3) R-value of ceiling insulation against & above the insulated duct ≥ R-value of ceiling insulation minus R-value of duct insulation
|  |  | Ductwork in ventilated space |  |  | Air handler located completely within continuous air barrier and within building thermal envelope
Duct leakage ≤1.5 cfm per 100 sf of conditioned floor area served by duct system
Where located against and above duct ceiling insulation R-value ≥ proposed ceiling insulation less duct insulation
|  |  | Ductwork in floor cavities over unconditioned space |  |  | Continuous air barrier installed between unconditioned space and duct.
Compliant floor insulation
≥R-19 separating duct from unconditioned space
|  |  | Ductwork located within exterior walls |  |  | Continuous air barrier installed between unconditioned space and duct.
≥R-10 separating duct from outside sheathing
Remainder of cavity insulation fully insulated to drywall side
|  |  | Ducts buried within ceiling insulation |  | Partially or completely buried | Where supply & return air ducts are partially or completely buried in ceiling insulation
[5 empty] | ≥R-8 on supply and return ducts | ≥R-8 duct insulation
[5 empty] | Sum of ceiling insulation against & above top of duct and against & below bottom of duct ≥R-19, excluding R-value of duct insulation | At all points along each duct, sum of ceiling insulation above and against top of duct and against and below bottom of duct ≥R-19 excluding duct insulation
|  |  | Effective R-value of deeply buried ducts |  | R-25 considered effective R-value | R-25 considered effective R-value
[5 empty] | Where using simulated energy performance analysis | Where using simulated energy performance analysis
[5 empty] | Ducts located on or within 5.5" of ceiling | Ducts located on or within 5.5" of ceiling
[5 empty] | Surrounded by blow-in attic insulation ≥R-30 with top of insulation ≥3.5" above top of duct | Surrounded by blow-in attic insulation ≥R-30 with top of insulation ≥3.5" above top of duct
Sealing (Mandatory)
|  |  | Ducts, air handlers & filter boxes | Sealed | Sealed | Sealed
Testing
|  |  | Post construction | ≤4 cfm per 100 sf of conditioned floor area across entire system | ≤4 cfm per 100 sf of conditioned floor area across entire system | ≤4.0 cfm per 100 sf of conditioned floor area across entire system
|  |  | Rough-in with air handler | ≤4 cfm per 100 sf of conditioned floor area across system | ≤4 cfm per 100 sf of conditioned floor area across system | ≤4.0 cfm per 100 sf of conditioned floor area across system
|  |  | Rough-in without air handler | ≤3 cfm per 100 sf of conditioned floor area | ≤3 cfm per 100 sf of conditioned floor area | ≤3.0 cfm per 100 sf of conditioned floor area
|  |  | All within thermal envelope |  |  | Total leakage ≤8.0 cfm per 100 sf of conditioned floor area
|  |  | Exception: | Testing not required for ducts & air handlers located entirely within building thermal envelope | Testing not required for ducts & air handlers located entirely within building thermal envelope
[5 empty] | Testing not required for heat or energy recovery ventilator ducts | Testing not required for ducts serving heating, cooling or ventilation systems not integrated with ducts serving heating & cooling systems
|  |  | Sealed air handler | Manufacturer's designation for leakage rate ≤2% of design air flow | Manufacturer's designation for leakage rate ≤2% of design air flow | Manufacturer's designation for leakage rate ≤2% of design air flow
|  |  | Building cavities (Mandatory) | Framing cavities not to be used as ducts or plenums | Framing cavities not to be used as ducts or plenums | Framing cavities not to be used as ducts or plenums
Mechanical system piping insulation (Mandatory)
|  | Insulation on piping capable of carrying fluids >105°F and <55°F |  | ≥R-3 | ≥R-3 | ≥R-3
|  | Insulation protection |  | From damage from sunlight, moisture, equipment maintenance and wind | From damage from sunlight, moisture, equipment maintenance and wind | From damage from sunlight, moisture, equipment maintenance and wind
|  |  |  | Shielded from solar radiation | Shielded from solar radiation | Shielded from solar radiation
|  |  |  | Adhesive tape not permitted | Adhesive tape not permitted | Adhesive tape not permitted
Service hot water systems
Circulating hot water systems (Mandatory)
|  |  | Circulation systems | Automatic controls, temperature sensors & pump to be accessible. | Automatic controls, temperature sensors & pump to be accessible. | Automatic controls, temperature sensors & pump to be accessible.
|  |  |  | Manual controls to be readily accessible | Manual controls to be readily accessible | Manual controls to be readily accessible
|  |  |  | Provided with circulation pump | Provided with circulation pump | Provided with circulation pump
|  |  |  | Gravity & thermosyphon circulation systems prohibited | Gravity & thermosyphon circulation systems prohibited | Gravity & thermosyphon circulation systems prohibited
|  |  |  | Controls start pump based on demand | Controls start pump based on demand | Controls start pump based on demand
|  |  |  | Controls automatically turn off pump when loop is at desired temperature & when there is no demand | Controls automatically turn off pump when loop is at desired temperature & when there is no demand | Controls automatically turn off pump when loop is at desired temperature & when there is no demand
|  |  | Heat trace systems | Controls to automatically adjust energy input to maintain desired water temperature when heated water is used in occupancy | Controls to automatically adjust energy input to maintain desired water temperature when heated water is used in occupancy | Controls to automatically adjust energy input to maintain desired water temperature when heated water is used in occupancy
|  |  | Demand recirculation systems | Pumps heated water from supply & back to source through cold water supply pipe | Pumps heated water from supply & back to source through cold water supply pipe | Pumps heated water from supply & back to source through cold water supply pipe
|  |  |  | Controls shall: | Controls shall: | Controls shall:
|  |  |  | 1) Start pump upon receiving signal from action of user, sensing presence of user, or sensing flow | 1) Start pump upon receiving signal from action of user, sensing presence of user, or sensing flow | 1) Start pump upon receiving signal from action of user, sensing presence of user, or sensing flow
|  |  |  | 2) Limit temperature entering cold water piping to 104°F | 2) Limit temperature entering cold water piping to 104°F | 2) Limit temperature entering cold water piping to 104°F
|  | Hot water pipe insulation (Prescriptive) |  | ≥R-3 on piping: | ≥R-3 on piping: | ≥R-3 on piping:
|  |  |  | 1) ≥¾" nominal diameter | 1) ≥¾" nominal diameter | 1) ≥¾" nominal diameter inside conditioned space
|  |  |  | 2) Serving >1 dwelling unit | 2) Serving >1 dwelling unit | 2) Serving >1 dwelling unit
|  |  |  | 3) Located outside conditioned space | 3) Located outside conditioned space | 3) Located outside conditioned space
|  |  |  | 4) From water heater to distribution manifold | 4) From water heater to distribution manifold | 4) From water heater to distribution manifold
|  |  |  | 5) Located under floor slab | 5) Located under floor slab | 5) Located under floor slab
|  |  |  | 6) Buried | 6) Buried | 6) Buried
|  |  |  | 7) Supply & return in recirculating systems other than demand recirculating systems | 7) Supply & return in recirculating systems other than demand recirculating systems | 7) Supply & return in recirculating systems other than demand recirculating systems
Drain water heat recovery units
|  |  | Potable water-side pressure loss | <3 psi for units connected to 1 or 2 showers | <3 psi for units connected to 1 or 2 showers | <3 psi for units connected to 1 or 2 showers
|  |  |  | <2 psi for units connected to ≥3 showers | <2 psi for units connected to ≥3 showers | <2 psi for units connected to ≥3 showers
Mechanical ventilation (Mandatory)
|  | Dampers on outdoor air intakes & exhausts |  | Automatic or gravity that close when system not operating | Automatic or gravity that close when system not operating | Automatic or gravity that close when system not operating
Whole-house mechanical ventilation system fan efficiency
|  |  | HRV or ERV |  | 1.2 cfm/watt | 1.2 cfm/watt
|  |  | Range hoods | 2.8 cfm/watt | 2.8 cfm/watt
|  |  | In-line fan | 2.8 cfm/watt | 2.8 cfm/watt | 3.8 cfm/watt
|  |  | Other exhaust fans <90 cfm |  |  | 2.8 cfm/watt
|  |  | Other exhaust fans ≥90 cfm |  |  | 3.5 cfm/watt
|  |  | Air handler integrated to HVAC equipment |  |  | 1.2 cfm/watt
Bathroom, utility room
|  |  | ≥10 & <90 cfm | 1.4 cfm/watt | 1.4 cfm/watt
|  |  | ≥90 cfm | 2.8 cfm/watt | 2.8 cfm/watt
|  |  | Exception: | Fans integral to tested & listed HVAC equipment | Fans integral to tested & listed HVAC equipment
|  |  |  | Air handler powered by electronically commutated motor | Air handler powered by electronically commutated motor
|  | Testing of mechanical ventilation systems |  |  |  | Verified to provide minimum
Performed per manufacturer's instructions or
Using flow hood or box, flow grid or other device
Conducted by approved 3rd party where required
Written report provided to code official
Equipment sizing and efficiency rating (mandatory)
|  | Equipment sizing (Mandatory) |  | Heating & cooling equipment | Heating & cooling equipment | Heating & cooling equipment
|  |  |  | Sized in accordance with ACCA Manual S | Sized in accordance with ACCA Manual S | Sized in accordance with ACCA Manual S
|  |  |  | Loads calculated in accordance with ACCA Manual J | Loads calculated in accordance with ACCA Manual J | Loads calculated in accordance with ACCA Manual J
|  |  |  | Or other approved calculation method | Or other approved calculation method | Or other approved calculation method
|  | Equipment efficiency |  | ≥Minimum required by federal law for the geographic location where installed | ≥Minimum required by federal law for the geographic location where installed | ≥Minimum required by federal law for the geographic location where installed
| Systems serving multiple dwelling units |  |  | Comply with Sections C403 & C404 | Comply with Sections C403 & C404 | Comply with Sections C403 & C404
| Snow melt system controls (Mandatory) |  |  | Snow & ice melting systems | Snow & ice melting systems | Snow & ice melting systems
|  |  | Automatic controls to turn off system when | Pavement temperature >50°F and | Pavement temperature >50°F and | Pavement temperature >50°F and
|  |  |  | No precipitation falling | No precipitation falling | No precipitation falling
|  |  | Automatic or manual control to allow shutoff when | Outdoor temperature >40°F | Outdoor temperature >40°F | Outdoor temperature >40°F
Pools & inground permanently installed spas (Mandatory)
|  |  |  | Accessory to one- and two family dwellings & townhouses ≤3 stories that are available only to household & guests | Accessory to one- and two family dwellings & townhouses ≤3 stories that are available only to household & guests | Pools and permanent spas energy consumption requirements of APSP 15
|  |  | Heaters | Readily accessible on-off switch mounted outside heater to | Readily accessible on-off switch mounted outside heater to | Readily accessible on-off switch mounted outside heater to
|  |  |  | allow shut off without adjusting thermostat setting | allow shut off without adjusting thermostat setting | allow shut off without adjusting thermostat setting
|  |  |  | No constant burning pilot on gas-fired units | No constant burning pilot on gas-fired units | No constant burning pilot on gas-fired units
|  |  | Time switches or other control method | Turn off & on heaters & pumps according to preset schedule | Turn off & on heaters & pumps according to preset schedule | Turn off & on heaters & pumps according to preset schedule
|  |  | Exceptions: | Required 24-hour operation by public health standard | Required 24-hour operation by public health standard | Required 24-hour operation by public health standard
|  |  |  | Required to operate solar and waste-heat-recovery pool heating systems | Required to operate solar and waste-heat-recovery pool heating systems | Required to operate solar and waste-heat-recovery pool heating systems
|  |  | Covers | Vapor-retardant cover | Vapor-retardant cover | Vapor-retardant cover
|  |  | Exception: | Deriving >70% heating energy from site-recovered energy over an operating season | Deriving >75% heating energy from site-recovered energy over an operating season | Deriving >75% heating energy from site-recovered energy over an operating season
|  |  | Portable spas |  |  | Energy consumption requirements of APSP 14
Electrical Power and Lighting Systems (Mandatory)
Lighting equipment (Mandatory)
|  | High-efficacy lamps |  | ≥75% lamps in permanently installed fixtures or |  | All permanently installed lighting fixtures, excluding kitchen appliances, contain only high-efficacy lighting sources
|  |  |  | In ≥75% permanently installed fixtures | In ≥90% permanently installed fixtures
|  | Fuel gas lighting system |  | No continuously burning pilot lights | No continuously burning pilot lights | No continuously burning pilot lights
|  | Exterior lighting for residential buildings |  |  |  | Comply with Section C405.4
Exceptions:
Detached one- & two-family dwellings
Townhouses
Solar-powered lamps not connected to any electric service
Luminaires controlled by motion sensor
Lamps & luminaires that comply with R404.1
|  | Exterior lighting controls |  |  |  | Where total permanently installed exterior lighting power >30 watts
Controlled by manual on & off switch which permits automatic shut-off actions
Automatically shut off when daylight is present & satisfies lighting needs
Override of automatic off not permitted unless returns to normal automatic operation within 24 hours
Simulated Performance Alternate (Performance)
|  |  |  | Allowed | Allowed | Allowed
Energy Rating Index (ERI)Compliance Alternative
|  | Mandatory requirements |  | Meet all mandatory requirements | Meet all mandatory requirements | Meet requirements of sections listed in Table R406.2
|  |  |  | ≥ thermal envelope efficiencies in 2009 IECC | ≥ thermal envelope efficiencies in 2009 IECC | Building thermal envelope where on-site renewables are not included:
UA of proposed total building thermal envelope ≤1.15 times UA of prescriptive reference design
Building thermal envelope where on-site renewables are included:
Building thermal envelope ≥ levels of efficiency & SHGC in prescriptive tables
|  |  | Exception: | ≥R-6 duct insulation outside thermal envelope | ≥R-6 duct insulation outside thermal envelope
|  | Energy Rating Index (ERI) |  |  |  | Energy used for recharge or refuel vehicles not included
|  |  |  | Consider all energy used | Consider all energy used | Energy use reduction associated with on-site renewable energy ≤5% total energy use
|  |  | ERI-based compliance | ≤55 | ≤61 | ≤52.25
[5 empty] | Where on-site renewable energy is included for compliance, building thermal envelope efficiencies ≥ 2015 IECC efficiencies | Is 55 from ERI table reduced by 5% for additional energy efficiency option
|  |  | Verification | By approved 3rd party | By approved 3rd party | BY AHJ or approved 3rd party
|  |  | Compliance report | Address / other identification | Address / other identification | For permit application
|  |  |  | Inspection checklist for component characteristics of rated design | Inspection checklist for component characteristics of rated design | Building street address or other site identification
|  |  |  | Inspection checklist show results for reference design and rated design | Inspection checklist show results for reference design and rated design | Declare ERI on title page & building plans
|  |  |  | Person completing compliance report | Person completing compliance report | Person performing analysis & generating compliance report
|  |  |  | Identify compliance software tool | Identify compliance software tool | Identify compliance software tool
Documentation of all inputs to produce results for reference design and/or rated home
Certificate indicating proposed design ERI ≤ required
Certificate documents building component energy specifications to be installed
When site-specific report not generated, proposed design based on worst-case orientation & configuration of rated home
Confirmed report for certificate of occupancy
Building street address or other site identification
Declare ERI on title page & building plans
Person performing analysis & generating compliance report
Identify compliance software tool
Documentation of all inputs to produce results for reference design and/or rated home
Certificate confirms energy features in home
|  |  | Renewable energy certificate (REC) documentation |  |  | Where on-site renewable energy included in ERI
One of forms submitted to code official:
1. Substantiation RECs are owned by or retired on behalf of homeowner
2. Contract conveying RECs to homeowner
Additional Efficiency Package Options
Enhanced envelope performance option
UA ≤ 0.95 × UAcode compliant
SHGCarea-weighted average ≤0.95 ×
SHGCcode compliant
More efficient HVAC equipment performance option
≥95 AFUE natural gas furnace
≥16 SEER air conditioner
≥10 HSPF/16 SEER air source heat pump
≥3.5 COP ground source heat pump
Reduced energy use in service water heating option
≥82 EF fossil fuel systems
≥2.0 EF electric systems
≥0.4 solar fraction solar systems
More efficient duct thermal distribution system option
100% of ducts & air handlers located within building thermal envelope
100% of ductless thermal distribution system or hydronic thermal distribution system located within building thermal envelope
100% duct thermal distribution system located in conditioned space
Improved air sealing and efficient ventilation system option
≤3.0 ACH50 with either ERV or HRV with minimum requirements measured at lowest net supply
≥75% SRE or
≤1.1 cfm per watt
Shall not use recirculation as defrost strategy
ERV: ≥50% LRMT
Existing Buildings
|  | New and replacement materials |  | Meet new construction requirements | Meet new construction requirements | Meet new construction requirements
|  |  |  | except where permitted by this code | except where permitted by this code | except where permitted by this code
Additions
|  | To buildings, building systems or portions thereof |  | Meet new construction requirements | Meet new construction requirements | Meet new construction requirements
|  |  |  | Compliance for addition alone, for addition and existing building as a single building or where building with addition uses no more energy than existing building | Compliance for addition alone, for addition and existing building as a single building or where building with addition uses no more energy than existing building | Compliance for addition alone, for addition and existing building as a single building or where building with addition uses no more energy than existing building
|  | Where nonconditioned space changed to conditioned space |  | Addition building envelope UA complies | Addition building envelope UA complies | Addition building envelope UA complies
|  |  |  | UA of existing building & addition and any alterations ≤UA for existing building | UA of existing building & addition and any alterations ≤UA for existing building | UA of existing building & addition and any alterations ≤UA for existing building
Heating and cooling systems
|  |  | New ducts | Comply with code | Comply with code | Comply with code
|  |  | Ducts from existing system in unconditioned space | <40 linear feet need not be tested | <40 linear feet need not be tested | Exception for ducts extended from existing system to addition
Service hot water system
|  |  | Systems part of addition | Comply with code | Comply with code | Comply with code
Lighting
|  |  | New systems part of addition | Comply with code | Comply with code | Comply with code
|  | Existing plus addition compliance (Simulated Performance Alternative) |  | Addition & Alteration comply entirely with Section R405 | Addition & Alteration comply entirely with Section R405 | Addition & Alteration comply entirely with Section R405
|  |  |  | Annual energy cost (or energy use) of addition & existing building with alterations ≤ cost (use) of existing building | Annual energy cost (or energy use) of addition & existing building with alterations ≤ cost (use) of existing building | Annual energy cost (or energy use) of addition & existing building with alterations ≤ cost (use) of existing building
Alterations
|  | To buildings, building systems or portions thereof |  | Meet new construction requirements | Meet new construction requirements | Meet new construction requirements
|  |  |  | Not increase energy use | Not increase energy use | Not increase energy use
Building envelope exceptions
|  |  |  | 1) Storm windows over existing fenestration | 1) Storm windows over existing fenestration | 1) Storm windows over existing fenestration
|  |  |  | 2) Existing cavities filled with insulation exposed during construction | 2) Existing cavities filled with insulation exposed during construction | 2) Existing cavities filled with insulation exposed during construction
|  |  |  | 3) Existing cavities not exposed during construction | 3) Existing cavities not exposed during construction | 3) Existing cavities not exposed during construction
|  |  |  | 4) Roof recover | 4) Roof recover | 4) Roof recover
|  |  |  | 5) Roofs without insulation in cavity & where sheathing or insulation is exposed during reroofing shall be insulated either above or below sheathing | 5) Roofs without insulation in cavity & where sheathing or insulation is exposed during reroofing shall be insulated either above or below sheathing | 5) Roofs without insulation in cavity & where sheathing or insulation is exposed during reroofing shall be insulated either above or below sheathing
|  |  |  | 6) Surface-applied window film on existing single pane fenestration | 6) Surface-applied window film on existing single pane fenestration | 6) Surface-applied window film on existing single pane fenestration
|  | Replacement fenestration |  | ≤U-0.32 | ≤U-0.3 | ≤U-0.3
|  | Heating and cooling systems |  | Comply with code | Comply with code | Comply with code
|  |  | Ducts from existing system in unconditioned space | <40 linear feet need not be tested | <40 linear feet need not be tested | Exception for ducts extended to addition
|  | Service hot water systems |  | Comply with code | Comply with code | Comply with code
|  | Lighting |  | Comply with code | Comply with code | Comply with code
|  |  | Exception | Replace <50% luminaires in space & not increase lighting power | Replace <50% luminaires in space & not increase lighting power | Replace <10% luminaires in space & not increase lighting power
|  | Change in space conditioning |  | Space bought into full compliance with code | Space bought into full compliance with code | Space bought into full compliance with code
|  |  | Exception | Where simulated performance option is used to comply & | Where simulated performance option is used to comply & | Where simulated performance option is used to comply &
|  |  |  | Proposed annual energy cost ≤110% otherwise allowed annual energy cost | Proposed annual energy cost ≤110% otherwise allowed annual energy cost | Proposed annual energy cost ≤110% otherwise allowed annual energy cost
Repairs
|  |  | Application (considered repairs) | Glass-only replacement in existing sash & frame | Glass-only replacement in existing sash & frame | Glass-only replacement in existing sash & frame
|  |  |  | Roof repairs | Roof repairs | Roof repairs
|  |  |  | Replace bulb and/or ballast within existing luminaires & not increase installed power | Replace bulb and/or ballast within existing luminaires & not increase installed power | Replace bulb and/or ballast within existing luminaires & not increase installed power
Change of Occupancy or use
|  |  |  | Change resulting in increased energy use must comply | Change resulting in increased energy use must comply | Change resulting in increased energy use must comply
|  |  |  | Change to dwelling unit or portion thereof from another use or occupancy must comply | Change to dwelling unit or portion thereof from another use or occupancy must comply | Change to dwelling unit or portion thereof from another use or occupancy must comply
Appendix RA
Recommended Procedure for Worst-Case Testing of Atmospheric Venting Systems Under R402.4 or R05 Conditions ≤5 ACH50
Recommended to identify problems that weaken draft & restrict combustion air
Where required by code official
Conducted by approved 3rd party
Conducted after creation of all penetrations & prior to final inspection
Appendix |  |  |  | Appendix RB | Appendix RA | Appendix RB
Solar-Ready Provisions - Detached One- and Two-Family Dwellings, Multiple Single-Family Dwellings (Townhouses)
|  | Solar-ready zone, definition |  | Section(s) of roof or overhang designated and reserved for future installation of solar photovoltaic or solar thermal | Section(s) of roof or overhang designated and reserved for future installation of solar photovoltaic or solar thermal | Section(s) of roof or overhang designated and reserved for future installation of solar photovoltaic or solar thermal
|  | General |  | New construction | New construction | New construction
|  |  |  | ≥600 sf of roof area oriented between 110° & 270° of true north | ≥600 sf of roof area oriented between 110° & 270° of true north | ≥600 sf of roof area oriented between 110° & 270° of true north
|  |  | Exceptions: | New residential buildings with permanently installed on-site renewable energy system | New residential buildings with permanently installed on-site renewable energy system | New residential buildings with permanently installed on-site renewable energy system
|  |  |  | Solar-ready zone shaded for >70% daylight hours annually | Solar-ready zone shaded for >70% daylight hours annually | Solar-ready zone shaded for >70% daylight hours annually
|  | Construction documents |  | Indicate solar-ready zone | Indicate solar-ready zone | Indicate solar-ready zone
|  |  | Solar-ready zone area (exclusive of mandatory access or set back areas required by IFC) | ≥300 sf | ≥300 sf | ≥300 sf
|  |  |  | ≥150 sf on townhouses with floor area ≤2,000 sf per dwelling unit | ≥150 sf on townhouses with floor area ≤2,000 sf per dwelling unit | ≥150 sf on townhouses with floor area ≤2,000 sf per dwelling unit
|  |  |  | ≥5' wide & ≥80 sf | ≥5' wide & ≥80 sf | ≥5' wide & ≥80 sf
|  |  | Obstructions | Free from | Free from | Free from
|  |  | Roof load documentation | Dead load & live load clearly indicated | Dead load & live load clearly indicated | Dead load & live load clearly indicated
|  |  | Interconnection pathway | Indicate pathways for routing conduit or plumbing | Indicate pathways for routing conduit or plumbing | Indicate pathways for routing conduit or plumbing
|  |  | Capped roof penetration sleeve |  |  | Provided adjacent to solar-ready zone on roof slope ≥1 in 12
|  |  | Electrical service reserved space in main electrical panel | Space for dual pole circuit breaker | Space for dual pole circuit breaker | Space for dual pole circuit breaker
|  |  |  | Labeled "For Future Solar Electric" | Labeled "For Future Solar Electric" | Labeled "For Future Solar Electric"
|  |  |  | Space located at opposite end from feeder input | Space located at opposite end from feeder input | Space located at opposite end from feeder input
|  |  | Construction document certification | Indicating solar-ready zone & other requirements posted near electrical distribution panel, water heater or other conspicuous location | Indicating solar-ready zone & other requirements posted near electrical distribution panel, water heater or other conspicuous location | Indicating solar-ready zone & other requirements posted near electrical distribution panel, water heater or other conspicuous location